## Annual Summary 02-03
2002-2003 FUEL & ELECTRICTY CONSUMPTION (FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-CCF | 0 | 0 | 0 | 13190 | 94500 | 117360 | 42450 | 740 | 1430 | 12070 | 78870 | 28810 | 389420
| COST-$ | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 20391.49 | 692.4 | 1148.62 | 11320.94 | 43318.33 | 16045.48 | 195060.3
| UNIT COST | 0 | 0 | 0 | 0.37509 | 0.41735 | 0.48422 | 0.48036 | 0.93568 | 0.80323 | 0.93794 | 0.54924 | 0.55694 | 0.5009
| CCF BTUS (x 1000) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 4245000 | 74000 | 143000 | 1207000 | 7887000 | 2881000 | 38942000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 59621 | 108230 | 102128 | 67144 | 12160 | 0 | 349283
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 32232 | 67196.53 | 70577.27 | 59104.78 | 8278.9 | 0 | 237389.48
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0.54061 | 0.62087 | 0.69107 | 0.88027 | 0.68083 | 0 | 0.67965
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 8943150 | 16234500 | 15319200 | 10071600 | 1824000 | 0 | 52392450
TOTAL HEATING BTU | QTY-BTU (x 1k) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
TOTAL HEATING COSTS |  | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
ELECTRICITY | QUANTITY-KWH | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 29 | 30 | 29 | 32 | 28 | 36 | 36 | 33 | 31 | 27 | 29 | 32 | 372
| KWH PER DAY | 36413.7931 | 42080 | 35172.4138 | 41550 | 35657.1429 | 35866.6667 | 23733.3333 | 34181.8182 | 40025.8065 | 36177.7778 | 37986.2069 | 31200 | 35638.7097
| COST-$ | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
| UNIT COST | 0.056584 | 0.053185 | 0.056844 | 0.048957 | 0.042418 | 0.042427 | 0.04776 | 0.044124 | 0.041885 | 0.046157 | 0.046457 | 0.052086 | 0.048117
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 2711 | 2653 | 2330 | 2778 | 2477 | 2136 | 2208 | 2112 | 2196 | 2134 | 2712 | 2292 | 28739
Demand (per 121 S Snelling Xcel billing) | COST - $ | 19993.39 | 21307.44 | 18878.6 | 21742.44 | 12443.62 | 12089.76 | 12497.28 | 11953.91 | 12429.36 | 14561.1 | 13454.6 | 12525.42 | 183876.92
| BTUS (x 1000) | 3603072 | 4307308.8 | 3480240 | 4536595.2 | 3406540.8 | 4405574.4 | 2915212.8 | 3848736 | 4233609.6 | 3332841.6 | 3758659.2 | 3406540.8 | 45234931.2 | 0
TOTAL CAMPUS BTU CONSUMPTION x 10 MIL |  | 3603.072 | 4307.3088 | 3480.24 | 5855.5952 | 12856.5408 | 16141.5744 | 16103.3628 | 20157.236 | 19695.8096 | 14611.4416 | 13469.6592 | 6287.5408 | 136569.3812
# STEAM GENERATED |  | 0 | 0 | 0 | 1295000 | 8481000 | 9980000 | 12296000 | 15826000 | 14626000 | 11696200 | 7625000 | 3217000 | 85042200
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 85.08% | 78.2% | 74.15% | 82.07% | 85.78% | 83.61% | 91.48% | 68.56% | 97.2% | 82.9%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 35 | 0 | 4 | 132 | 725 | 977 | 1200 | 1540 | 1372 | 1043 | 529 | 230 | 7787
COOLING DEGREE DAY - ACTUAL (MAC) |  | 199 | 348 | 172 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 859
Chiller - New Central Plant |  | 360 | 502 | 548 | 246 | 26 | 0 | 0 | 0 | 0 | 0 | 74 | 117 | 1873
Run - Old Central Plant |  | 277 | 184 | 330 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1091
Times - Chapel |  | 0 | 137 | 90 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299
2001-2002 FUEL & ELECTRICTY CONSUMPTION
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY - CCF | 0 | 0 | 0 | 12355 | 79249 | 85649 | 138479 | 146392 | 115013 | 136931 | 84306 | 41747 | 840121
| COST - $ | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54106.08 | 59123.34 | 45413.41 | 52101.56 | 33196.17 | 16235.31 | 318456.685
| UNIT COST | 0 | 0 | 0 | 0.31173 | 0.23297 | 0.40982 | 0.39072 | 0.40387 | 0.39485 | 0.38049 | 0.39376 | 0.3889 | 0.37906
| CCF BTUS (x 1000) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13847900 | 14639200 | 11501300 | 13693100 | 8430600 | 4174700 | 84012100
#2 FUEL OIL | QUANTITY - GAL | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 3006 | 0 | 3086
| COST - $ | 0 | 0 | 0 | 0 | 0 | 0 | 58.4 | 0 | 0 | 0 | 2194.38 | 0 | 2252.78
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 0 | 0 | 0 | 0.73 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 11040 | 0 | 0 | 0 | 414828 | 0 | 425868
#6 FUEL OIL | QUANTITY - GAL | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 6522 | 0 | 0 | 0 | 6542
| COST - $ | 0 | 0 | 0 | 0 | 0 | 0 | 17.8 | 0 | 5804.58 | 0 | 0 | 0 | 5822.38
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0 | 0.89 | 0 | 0 | 0 | 0.89
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 978300 | 0 | 0 | 0 | 978300
TOTAL HEATING BTU | QTY - BTU (x 1000) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13858940 | 14639200 | 12479600 | 13693100 | 8845428 | 4174700 | 85416268
TOTAL HEATING COSTS |  | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54182.28 | 59123.34 | 51217.99 | 52101.56 | 35390.55 | 16235.31 | 326531.845
ELECTRICITY | QUANTITY-KWH | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 34 | 27 | 23 | 31 | 33 | 27 | 38 | 24 | 30 | 33 | 28 | 358
| KWH PER DAY | 33360 | 40164.7059 | 34222.2222 | 36417.3913 | 39716.129 | 33818.1818 | 31733.3333 | 34042.1053 | 38600 | 36480 | 37672.7273 | 30342.8571 | 35584.3575
| COST-$ | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
| UNIT COST | 0.06052 | 0.058992 | 0.063424 | 0.052792 | 0.048759 | 0.045001 | 0.048318 | 0.046576 | 0.043553 | 0.044565 | 0.043432 | 0.048323 | 0.05024
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 2230 | 2230 | 2230 | 2230 | 2001 | 2136 | 2105 | 2093 | 2133 | 2081 | 2500 | 1970 | 25939
Demand (per 121 S Snelling Xcel billing) | COST - $ | 18531.3 | 18531.3 | 18531.3 | 14207.33 | 13213.26 | 12089.76 | 11914.3 | 15400 | 9658.22 | 11778.46 | 14081 | 11150.2 | 169086.43
| BTUS (x 1000) | 3414729.6 | 4659427.2 | 3152688 | 2857891.2 | 4200854.4 | 3807792 | 2923401.6 | 4413763.2 | 3160876.8 | 3734092.8 | 4241798.4 | 2898835.2 | 43466150.4
TOTAL CAMPUS BTU CONSUMPTION x 10 MIL |  | 3414.7296 | 4659.4272 | 3152.688 | 4093.3912 | 12125.7544 | 12372.692 | 16782.3416 | 19052.9632 | 15640.4768 | 17427.1928 | 13087.2264 | 7073.5352 | 128882.4184
# STEAM GENERATED |  | 0 | 0 | 0 | 1751000 | 9250000 | 806900 | 12313000 | 13582000 | 11274000 | 1299100 | 6827000 | 3256000 | 60359000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 0% | 103% | 86% | 80% | 85% | 81% | 82% | 72% | 68% | 73%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 63 | 9 | 5 | 183 | 513 | 301 | 1148 | 1234 | 1014 | 1239 | 615 | 357 | 6681
COOLING DEGREE DAY - ACTUAL (MAC) |  | 175 | 309 | 267 | 44 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 851
Chiller - New Central Plant |  | 349 | 495 | 490 | 209 | 4 | 0 | 0 | 0 | 0 | 0 | 52 | 82 | 1681
Run - Old Central Plant |  | 230 | 345 | 331 | 101 | 3 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 1030
Times - Chapel |  | 3 | 67 | 101.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179.5

## Summary page breaks
2002-2003 FUEL & ELECTRICTY CONSUMPTION (FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-CCF | 0 | 0 | 0 | 13190 | 94500 | 117360 | 42450 | 740 | 1430 | 12070 | 78870 | 28810 | 389420
| COST-$ | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 20391.49 | 692.4 | 1148.62 | 11320.94 | 43318.33 | 16045.48 | 195060.3
| UNIT COST | 0 | 0 | 0 | 0.37509 | 0.41735 | 0.48422 | 0.48036 | 0.93568 | 0.80323 | 0.93794 | 0.54924 | 0.55694 | 0.5009
| CCF BTUS (x 1000) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 4245000 | 74000 | 143000 | 1207000 | 7887000 | 2881000 | 38942000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 59621 | 108230 | 102128 | 67144 | 12160 | 0 | 349283
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 32232 | 67196.53 | 70577.27 | 59104.78 | 8278.9 | 0 | 237389.48
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0.54061 | 0.62087 | 0.69107 | 0.88027 | 0.68083 | 0 | 0.67965
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 8943150 | 16234500 | 15319200 | 10071600 | 1824000 | 0 | 52392450
TOTAL HEATING BTU | QTY-BTU (x 1k) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
TOTAL HEATING COSTS |  | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
ELECTRICITY | QUANTITY-KWH | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 29 | 30 | 29 | 32 | 28 | 36 | 36 | 33 | 31 | 27 | 29 | 32 | 372
| KWH PER DAY | 36413.7931 | 42080 | 35172.4138 | 41550 | 35657.1429 | 35866.6667 | 23733.3333 | 34181.8182 | 40025.8065 | 36177.7778 | 37986.2069 | 31200 | 35638.7097
| COST-$ | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
| UNIT COST | 0.056584 | 0.053185 | 0.056844 | 0.048957 | 0.042418 | 0.042427 | 0.04776 | 0.044124 | 0.041885 | 0.046157 | 0.046457 | 0.052086 | 0.048117
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 2711 | 2653 | 2330 | 2778 | 2477 | 2136 | 2208 | 2112 | 2196 | 2134 | 2712 | 2292 | 28739
Demand (per 121 S Snelling Xcel billing) | COST - $ | 19993.39 | 21307.44 | 18878.6 | 21742.44 | 12443.62 | 12089.76 | 12497.28 | 11953.91 | 12429.36 | 14561.1 | 13454.6 | 12525.42 | 183876.92
| BTUS (x 1000) | 3603072 | 4307308.8 | 3480240 | 4536595.2 | 3406540.8 | 4405574.4 | 2915212.8 | 3848736 | 4233609.6 | 3332841.6 | 3758659.2 | 3406540.8 | 45234931.2
TOTAL CAMPUS BTU CONSUMPTION x 10 MIL |  | 3603.072 | 4307.3088 | 3480.24 | 5855.5952 | 12856.5408 | 16141.5744 | 16103.3628 | 20157.236 | 19695.8096 | 14611.4416 | 13469.6592 | 6287.5408 | 136569.3812
# STEAM GENERATED |  | 0 | 0 | 0 | 1295000 | 8481000 | 9980000 | 12296000 | 15826000 | 14626000 | 11696200 | 7625000 | 3217000 | 85042200
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 85.08% | 78.2% | 74.15% | 82.07% | 85.78% | 83.61% | 91.48% | 68.56% | 97.2% | 82.9%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 35 | 0 | 4 | 132 | 725 | 977 | 1200 | 1540 | 1372 | 1043 | 529 | 230 | 7787
COOLING DEGREE DAY - ACTUAL (MAC) |  | 199 | 348 | 172 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 14 | 859
Chiller - New Central Plant |  | 360 | 502 | 548 | 246 | 26 | 0 | 0 | 0 | 0 | 0 | 74 | 117 | 1873
Run - Old Central Plant |  | 277 | 184 | 330 | 211 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 1091
Times - Chapel |  | 0 | 137 | 90 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 299
2001-2002 FUEL & ELECTRICTY CONSUMPTION
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY - CCF | 0 | 0 | 0 | 12355 | 79249 | 85649 | 138479 | 146392 | 115013 | 136931 | 84306 | 41747 | 840121
| COST - $ | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54106.08 | 59123.34 | 45413.41 | 52101.56 | 33196.17 | 16235.31 | 318456.685
| UNIT COST | 0 | 0 | 0 | 0.31173 | 0.23297 | 0.40982 | 0.39072 | 0.40387 | 0.39485 | 0.38049 | 0.39376 | 0.3889 | 0.37906
| CCF BTUS (x 1000) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13847900 | 14639200 | 11501300 | 13693100 | 8430600 | 4174700 | 84012100
#2 FUEL OIL | QUANTITY - GAL | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 3006 | 0 | 3086
| COST - $ | 0 | 0 | 0 | 0 | 0 | 0 | 58.4 | 0 | 0 | 0 | 2194.38 | 0 | 2252.78
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 0 | 0 | 0 | 0.73 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 11040 | 0 | 0 | 0 | 414828 | 0 | 425868
#6 FUEL OIL | QUANTITY - GAL | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 6522 | 0 | 0 | 0 | 6542
| COST - $ | 0 | 0 | 0 | 0 | 0 | 0 | 17.8 | 0 | 5804.58 | 0 | 0 | 0 | 5822.38
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0.89 | 0 | 0.89 | 0 | 0 | 0 | 0.89
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 978300 | 0 | 0 | 0 | 978300
TOTAL HEATING BTU | QTY - BTU (x 1000) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13858940 | 14639200 | 12479600 | 13693100 | 8845428 | 4174700 | 85416268
TOTAL HEATING COSTS |  | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54182.28 | 59123.34 | 51217.99 | 52101.56 | 35390.55 | 16235.31 | 326531.845
ELECTRICITY | QUANTITY-KWH | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 34 | 27 | 23 | 31 | 33 | 27 | 38 | 24 | 30 | 33 | 28 | 358
| KWH PER DAY | 33360 | 40164.7059 | 34222.2222 | 36417.3913 | 39716.129 | 33818.1818 | 31733.3333 | 34042.1053 | 38600 | 36480 | 37672.7273 | 30342.8571 | 35584.3575
| COST-$ | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
| UNIT COST | 0.06052 | 0.058992 | 0.063424 | 0.052792 | 0.048759 | 0.045001 | 0.048318 | 0.046576 | 0.043553 | 0.044565 | 0.043432 | 0.048323 | 0.05024
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 2230 | 2230 | 2230 | 2230 | 2001 | 2136 | 2105 | 2093 | 2133 | 2081 | 2500 | 1970 | 25939
Demand (per 121 S Snelling Xcel billing) | COST - $ | 18531.3 | 18531.3 | 18531.3 | 14207.33 | 13213.26 | 12089.76 | 11914.3 | 15400 | 9658.22 | 11778.46 | 14081 | 11150.2 | 169086.43
| BTUS (x 1000) | 3414729.6 | 4659427.2 | 3152688 | 2857891.2 | 4200854.4 | 3807792 | 2923401.6 | 4413763.2 | 3160876.8 | 3734092.8 | 4241798.4 | 2898835.2 | 43466150.4
TOTAL CAMPUS BTU CONSUMPTION x 10 MIL |  | 3414.7296 | 4659.4272 | 3152.688 | 4093.3912 | 12125.7544 | 12372.692 | 16782.3416 | 19052.9632 | 15640.4768 | 17427.1928 | 13087.2264 | 7073.5352 | 128882.4184
# STEAM GENERATED |  | 0 | 0 | 0 | 1751000 | 9250000 | 806900 | 12313000 | 13582000 | 11274000 | 1299100 | 6827000 | 3256000 | 60359000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 0% | 103% | 86% | 80% | 85% | 81% | 82% | 72% | 68% | 73%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 63 | 9 | 5 | 183 | 513 | 301 | 1148 | 1234 | 1014 | 1239 | 615 | 357 | 6681
COOLING DEGREE DAY - ACTUAL (MAC) |  | 175 | 309 | 267 | 44 | 1 | 0 | 0 | 0 | 0 | 0 | 20 | 35 | 851
Chiller - New Central Plant |  | 349 | 495 | 490 | 209 | 4 | 0 | 0 | 0 | 0 | 0 | 52 | 82 | 1681
Run - Old Central Plant |  | 230 | 345 | 331 | 101 | 3 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 1030
Times - Chapel |  | 3 | 67 | 101.5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179.5

## KWH Consumption
Electricity kwh
Year | June | July | August | September | October | November | December | January | February | March | April | May | Total
1991-92 (10,699,200 kwh) | 789600 | 1024800 | 878400 | 976800 | 873600 | 890400 | 931200 | 724800 | 1027200 | 818400 | 952800 | 811200 | 10699200
1992-93 (10,420,800 kwh) | 715200 | 861600 | 681600 | 876000 | 768000 | 988800 | 912000 | 914400 | 1089600 | 888000 | 957600 | 768000 | 10420800
1993-94 (10,384,173 kwh) | 722400 | 741600 | 782400 | 905013 | 935180 | 896884 | 915796 | 870500 | 1070400 | 825600 | 847200 | 871200 | 10384173
1994-95 (10,454,200 kwh) | 820800 | 763000 | 868800 | 957600 | 686400 | 955200 | 1018286 | 925714 | 981600 | 871200 | 955200 | 650400 | 10454200
1995-96 (10,836,825 kwh) | 840000 | 843200 | 768800 | 792525 | 924000 | 955460 | 987320 | 987320 | 972580 | 972500 | 947890 | 845230 | 10836825
1996-97 (11,988,879 kwh) | 727680 | 1204800 | 691200 | 1070400 | 960000 | 998400 | 1039898 | 1074562 | 1135139 | 1036800 | 972000 | 1078000 | 11988879
1997-98 (12,782,400 kwh) | 940800 | 979200 | 1008000 | 1135200 | 1144800 | 1096800 | 1195200 | 936000 | 1034400 | 1161600 | 1039200 | 1111200 | 12782400
1998-99 (12,979,200 kwh) | 1012800 | 1022400 | 1212000 | 1128000 | 1128000 | 945600 | 1195200 | 1056000 | 1101600 | 1039200 | 1130400 | 1008000 | 12979200
1999-00 (12,117,600 kwh) | 974400 | 1123200 | 1125600 | 1096800 | 1020000 | 1099200 | 849600 | 1020000 | 1039200 | 936000 | 878400 | 955200 | 12117600
2000-01 (11,611,968 kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
2001-02 (12,739,200 kwh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
2002-03 (13,257,600 kwh) | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
TOTAL | 977760 | 1109760 | 1147680 | 1017734.4 | 1086758.4 | 1026739.2 | 1038758.4 | 993657.6 | 1026240 | 984768 | 1067904 | 968313.6 | 12446073.6

## 3 yr KWH Chart
JUN JUL AUG SEP OCT NOV DEC JAN FEB MAR APR MAY
MAY
11,611,968Kwh
11,611,968Kwh
11611968
Kwh
12,117,900Kwh

## Electrical Cost
COST | B | C | D | E | F | G |  | H | I | J | K | L | M
ELECTRICITY TOTAL COST
YEAR | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1989-90 | 40002.4 | 43554.85 | 39046.44 | 47470.22 | 36457.51 | 40253.02 | 39151.3 | 34274.9 | 32454.02 | 25671.79 | 38774.29 | 45942.72 | 463053.46
1991-92 | 41113.47 | 50860.74 | 47208.14 | 49653.69 | 37847.85 | 37085.37 | 36864.35 | 30817.13 | 39190.54 | 33672.49 | 37280.92 | 32377.89 | 473972.58
1992-93 | 38314.85 | 42152.25 | 37079.75 | 46777.86 | 33218.57 | 40339.61 | 37360.15 | 39558.76 | 46266.57 | 38935.94 | 43266.57 | 36921.27 | 480192.15
1993-94 | 40091.94 | 40591.98 | 44375.95 | 43186.49 | 44626.02 | 41549.88 | 40723.46 | 37921.42 | 44894.64 | 36792.89 | 37620.55 | 35346.3 | 487721.52
1994-95 | 45600.2 | 44893.52 | 52046.86 | 52102.41 | 31287.66 | 42689.29 | 43780.36 | 39800.33 | 40413.64 | 39014.34 | 41888.24 | 34366.22 | 507883.07
1995-96 | 46925.95 | 51452.69 | 46912.74 | 43310.12 | 41541.3 | 41915.28 | 43312.45 | 43312.45 | 41359.76 | 43473.7 | 43714.81 | 44719.41 | 531950.66
1996-97 ($559,179) | 36089.46 | 55056.45 | 46912.74 | 56136.57 | 44123.69 | 45668.97 | 44214.67 | 45688.5 | 47543.95 | 44095.82 | 46660.08 | 46988.51 | 559179.41
1997-98 ($613,894) | 51716.17 | 50880.21 | 52281.52 | 64303.48 | 56190.32 | 49899.49 | 50752.79 | 42517.47 | 46017.2 | 48439.02 | 48518 | 52378.32 | 613893.99
1998-99 ($626,968) | 56859.53 | 54769.44 | 61577.19 | 61033.56 | 52785.32 | 46722.9 | 51000.75 | 45236.65 | 49097.71 | 47346.81 | 53244.68 | 47022.4 | 626696.94
1999-00 ($621,699) | 51795.48 | 60748.07 | 59773.29 | 64595.98 | 52768.07 | 51195.01 | 51791.91 | 46138.66 | 47863.36 | 45512.26 | 47971.26 | 41545.57 | 621698.92
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($640,022) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
2002-03 ($637,914) | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
TOTAL | 55882.598 | 64320.708 | 62718.968 | 55923.49 | 49651.336 | 48492.78 | 46645.836 | 47304.328 | 47994.466 | 42906.486 | 51060.576 | 45874.858 | 618776.43

## KW Demand
ELECTRICITY KW | B | C | D | E | F | G | H | I | J | K | L | M | N
YEAR | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1991-92 | 1940 | 1940 | 2040 | 2112 | 1800 | 1704 | 1704 | 1704 | 1656 | 1704 | 1704 | 2112 | 22120
1992-93 | 1968 | 1920 | 1968 | 2112 | 2040 | 1824 | 1800 | 1704 | 1776 | 1752 | 1776 | 1992 | 22632
1993-94 | 1968 | 1944 | 2112 | 1920 | 1920 | 1752 | 1752 | 1752 | 1872 | 1776 | 1776 | 1944 | 22488
1995-96 | 1992 | 2088 | 2088 | 1992 | 1608 | 1776 | 1776 | 1776 | 1776 | 1920 | 1920 | 1992 | 22704
1996-97 | 2064 | 2136 | 2184 | 2280 | 1968 | 2112 | 1968 | 1968 | 1896 | 1920 | 2256 | 1896 | 24648
1997-98 | 2232 | 2280 | 2040 | 2592 | 2592 | 2256 | 2040 | 1872 | 1992 | 2016 | 2208 | 2328 | 26448
1998-99 | 2376 | 2208 | 2280 | 2448 | 2208 | 2208 | 1920 | 1824 | 2040 | 2016 | 2256 | 2328 | 26112
1999-2000
2000-2001
2001-2002
2002-03 | 2711 | 2653 | 2330 | 2778 | 2477 | 2136 | 2208 | 2112 | 2196 | 2134 | 2712 | 2292 | 28739
TOTAL | 2224 | 2208 | 2168 | 2440 | 2256 | 2192 | 1976 | 1888 | 1976 | 1984 | 2240 | 2184 | 25736

## KW Cost
ELECTRICITY KW COST
YEAR | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER |  | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1992-93 | 15192.96 | 14822.4 | 15192.96 | 11302.08 | 10423.68 | 9959.04 |  | 9828 | 9303.84 | 9696.96 | 9565.92 | 9696.96 | 10876.32 | 135861.12
1993-94 | 15195.96 | 14822.4 | 16304.34 | 12968.46 | 12968.46 | 9565.92 |  | 9565.92 | 9565.92 | 10221.12 | 9696.96 | 10052.16 | 11003.04 | 141930.66
1994-95 | 16553.52 | 19086.41 | 17929.65 | 14404.55 | 10019.17 | 11003 |  | 11369.81 | 11369.81 | 12669.7 | 11229.44 | 11740.28 | 13838.76 | 161214.1
1995-96 | 16553 | 19086 | 17929 | 14404 | 10019 | 11003 |  | 11369 | 11369 | 12669 | 11229 | 11740 | 13868 | 161238
1996-97 | 13721 | 17158 | 18149 | 18947 | 11138 | 11954 |  | 11510 | 11510 | 11320 | 10867 | 12769 | 10731 | 159774
1997-98 | 18547 | 18947 | 16952 | 21539 | 14670 | 12769 |  | 11546 | 10595 | 11275 | 11411 | 12497 | 13176 | 173924
1998-99 | 19744.56 | 18348.48 | 18946.8 | 20342.88 | 12497.82 | 12497.28 |  | 10867.2 | 10323.84 | 11546 | 11411 | 12769 | 13176 | 172470.86
1999-2000
2000-2001 | 17550.72 | 18531.3 | 23593.75 | 14963.35 | 10595.52 | 10595.52 | 10052.15 | 10595.52 | 10609.1 | 7607.04 | 12361.44 | 8422.08 | 155477.49 | 310954.98
2001-2002 | 19013.9 | 20473.14 | 19784.5 | 14532.82 | 13255.72 | 12089.76 | 11914.3 | 15400.28 | 9658.22 | 11778.46 | 14080.8 | 11150.2 | 173132.1 | 346264.2
2002-2003 | 19993.39 | 21307.44 | 18878.6 | 21742.44 | 12443.62 | 12089.76 | 12497.28 | 11953.91 | 12429.36 | 14561.1 | 13454.6 | 12525.42 | 183876.92 | 367753.84
TOTAL | 18852.67 | 20103.96 | 20752.2833 | 17079.5367 | 12098.2867 | 11591.68 | 11487.91 | 12649.9033 | 10898.8933 | 11315.5333 | 13298.9467 | 10699.2333 | 170828.8367 | 341657.6733

## 3 yr Elec Cost-Consump
3 YEAR ELECTRICAL COST/CONSUMPTION COMPARISON

## ELECOMs
1996-97 ($559,179) | 36089.46 | 55056.45 | 46912.74 | 56136.57 | 44123.69 | 45668.97 | 44214.67 | 45688.5 | 47543.95 | 44095.82 | 46660.08 | 46988.51
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
1997-98 ($613,894) | 51716.17 | 50880.21 | 52281.52 | 64303.48 | 56109.32 | 49899.49 | 50752.79 | 42517.47 | 46017.2 | 48439.02 | 48518 | 52378.32
1998-99 ($626,696) | 56859.53 | 54769.44 | 61577.19 | 61033.56 | 52785.32 | 46722.9 | 51000.75 | 45236.65 | 49097.71 | 47346.81 | 53244.68 | 52378.32
1999-00 ($621,699) | 51795.48 | 60748.07 | 59773.29 | 64595.98 | 52768.07 | 51195.01 | 51791.91 | 46138.66 | 47863.36 | 45512.26 | 47971.26 | 41545.57 | 621698.92
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($642,002) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
1996-97 | 727680 | 1204800 | 691200 | 1070400 | 960000 | 998400 | 1039898 | 1074562 | 1135139 | 1036800 | 972000 | 1078000 | 11988879
1997-98 (12,782,400Kwh) | 940800 | 979200 | 1008000 | 1135200 | 1144800 | 1096800 | 1195200 | 936000 | 1034400 | 1161600 | 1039200 | 1111200 | 12782400
1998-99 (12,972,000Kwh) | 1012800 | 1022400 | 1212000 | 1128000 | 1128000 | 945600 | 1195200 | 1056000 | 1101600 | 1039200 | 1130400 | 1000800 | 12972000
1999-00 (12,117,600Kwh) | 974400 | 1123200 | 1125600 | 1096800 | 1020000 | 1099200 | 849600 | 1020000 | 1039200 | 936000 | 878400 | 955200 | 12117600
2000-01 (11,611,968Kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
2001-02 (12,739,200Kwh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($642,002) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
2002-03 ($637,914) | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
2000-01 (11,611,968Kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
2001-02 (12,739,200Kwh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
2002-03 (13,257,600 kwh) | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600

## Fuel Costs
COST OF GAS AND OIL
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1989-90 | 0 | 0 | 1671.63 | 7253.34 | 17630.36 | 32716.96 | 42366.81 | 44027.01 | 34538.38 | 27473.6 | 16807.89 | 5040.52 | 229526.5
1990-91 | 0 | 0 | 291.5 | 3837.1 | 16924.99 | 31880.28 | 46660.15 | 52425.97 | 38789.76 | 38003.13 | 15708.77 | 3301.84 | 247823.49
1991-92 | 290.13 | 290.13 | 290.13 | 2866.55 | 13910.59 | 24580.49 | 26474.94 | 29092.45 | 23169.06 | 19766.86 | 14441.43 | 4598 | 159770.76
1992-93 | 288.75 | 288.75 | 1392.574 | 8056.64 | 24858.19 | 33944.9 | 36597.08 | 37666.34 | 40480.24 | 39229.84 | 28818.27 | 7191.31 | 258812.884
1993-94 | 293.25 | 293.25 | 697.82 | 6527.91 | 19150.61 | 29301.55 | 31912.22 | 40397.79 | 35193.32 | 27280 | 16273.2 | 4786.13 | 212107.05
1994-95 | 288.75 | 288.75 | 1151.1 | 2292.35 | 10657.36 | 21758.26 | 30701.63 | 27292.94 | 19216.89 | 20358.27 | 16902.56 | 4753.26 | 155662.12
1995-96 | 288.75 | 288.75 | 288.75 | 4332.94 | 14332.72 | 26743.22 | 26190.43 | 32872.05 | 38188.42 | 34119.99 | 26100.05 | 8030.53 | 211776.6
1996-97 | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04 | 293146.26
1997-98 | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46 | 220834.4
1998-99 | 288.75 | 288.76 | 288.75 | 2018.24 | 18469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 199452.77
1999-00 ($221,413) | 288.75 | 288.755 | 288.75 | 983.5 | 20197.96 | 28859.89 | 35145.45 | 42257.41 | 36007.86 | 28525.76 | 24229.36 | 4339.67 | 221413.115
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($326,532) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54182.28 | 59123.34 | 51217.99 | 52101.56 | 35390.55 | 16235.31 | 326531.845
2002-03 ($432,450) | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
TOTAL | 288.75 | 288.754 | 292.75 | 1947.71 | 22709.106 | 39089.414 | 52400.994 | 54254.934 | 45979.748 | 41512.722 | 27652.118 | 8621.834 | 295038.834

## BTUCOMS
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
BTU CONSUMPTION (X100k) | [12 empty] | (x1,000,000)
1990-91 | 614 | 1002 | 0 | 1928 | 7874 | 11939 | 17525 | 19717 | 14558 | 14259 | 7891 | 1431 | 98738
1991-92 | 0 | 0 | 0 | 1202 | 7265 | 17945 | 14660 | 14841 | 13590 | 11751 | 8715 | 2299 | 92268
1992-93 | 0 | 0 | 409 | 2964 | 7393 | 12550 | 15372 | 16846 | 15458 | 9169 | 13671 | 2144 | 95976
1993-94 | 0 | 0 | 159 | 2305 | 7588 | 11335 | 12733 | 16627 | 14967 | 10545 | 6351 | 1961 | 84571
1994-95 | 0 | 0 | 275 | 1031 | 5650 | 9983 | 13049 | 14129 | 11594 | 10552 | 8831 | 2351 | 77445
1995-96 | 0 | 0 | 224 | 2249 | 7187 | 12545 | 13706 | 16049 | 14292 | 13114 | 9072 | 3371 | 91809
1996-97 | 0 | 0 | 0 | 0 | 8136 | 15131 | 17211 | 18573 | 14593 | 13176 | 7953 | 5218 | 99991
1997-98 | 0 | 0 | 0 | 0 | 6058 | 13793 | 14768 | 15811 | 11057 | 12651 | 6650 | 1626 | 82414
1998-99 | 0 | 0 | 0 | 901 | 7039 | 11084 | 15072 | 18574 | 12758 | 11701 | 7595 | 1964 | 86688
TOTAL | 68.2222 | 111.3333 | 118.5556 | 1397.7778 | 7132.2222 | 12922.7778 | 14899.5556 | 16796.3333 | 13651.8889 | 11879.7778 | 8525.4444 | 2485 | 89988.8889
COST OF GAS AND OIL
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1989-90 | 0 | 0 | 1671.63 | 7253.34 | 17630.36 | 32716.96 | 42366.81 | 44027.01 | 34538.38 | 27473.6 | 16807.89 | 5040.52 | 229526.5
1990-91 | 0 | 0 | 291.5 | 3837.1 | 16924.99 | 31880.28 | 46660.15 | 52425.97 | 38789.76 | 38003.13 | 15708.77 | 3301.84 | 247823.49
1991-92 | 290.13 | 290.13 | 290.13 | 2866.55 | 13910.59 | 24580.49 | 26474.94 | 29092.45 | 23169.06 | 19766.86 | 14441.43 | 4598 | 159770.76
1992-93 | 288.75 | 288.75 | 1392.574 | 8056.64 | 24858.19 | 33944.9 | 36597.08 | 37666.34 | 40480.24 | 39229.84 | 28818.27 | 7191.31 | 258812.884
1993-94 | 293.25 | 293.25 | 697.82 | 6527.91 | 19150.61 | 29301.55 | 31912.22 | 40397.79 | 35193.32 | 27280 | 16273.2 | 4786.13 | 212107.05
1994-95 | 288.75 | 288.75 | 1151.1 | 2292.35 | 10657.36 | 21758.26 | 30701.63 | 27292.94 | 19216.89 | 20358.27 | 16902.56 | 4753.26 | 155662.12
1995-96 | 288.75 | 288.75 | 288.75 | 4332.94 | 14332.72 | 26743.22 | 26190.43 | 32872.05 | 38188.42 | 34119.99 | 26100.05 | 8030.53 | 211776.6
1996-97 | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04 | 293146.26
1997-98 | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46 | 220834.4
1998-99 | 288.75 | 288.76 | 288.75 | 2018.24 | 18469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 199452.77
TOTAL | 174.426 | 174.426 | 868.7308 | 5708.308 | 18494.948 | 30484.836 | 36802.24 | 40721.912 | 34434.152 | 30350.686 | 18409.912 | 4983.56 | 127424.15
1996-97 (99.99 BIL Btus) | 0 | 0 | 0 | 0 | 8136 | 15131 | 17211 | 18573 | 14593 | 13176 | 7953 | 5218
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
1997-98 (82.41 BIL Btus) | 0 | 0 | 0 | 0 | 6058 | 13793 | 14768 | 15811 | 11057 | 12651 | 6650 | 1626
1998-99 (86.67 BIL Btus) | 0 | 0 | 0 | 901400 | 7039200 | 11084400 | 15061736 | 18574200 | 12758000 | 11700800 | 7595200 | 1964300 | 86679236
1999-00 (76.96 BIL Btus) | 0 | 0 | 0 | 220900 | 6917400 | 8867600 | 13369310 | 16118600 | 12526905 | 9955900 | 7720300 | 1262900 | 76959815
2000-01 (94.7 BIL Btus) | 0 | 0 | 0 | 468000 | 6354800 | 12605900 | 19682500 | 15766350 | 15803900 | 13307450 | 8176900 | 2535700 | 94701500
2001-02 (84.2 BIL Btus) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13970210 | 14639200 | 11545805 | 13693100 | 8430600 | 4174700 | 84178915
1996-97 ($293,146) | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04
1997-98 ($220,834) | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46
1998-99 ($197,453) | 288.75 | 288.76 | 288.75 | 2018.24 | 16469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 197452.77
1999-00 ($221,394) | 288.75 | 288.755 | 288.75 | 983.5 | 20197.96 | 28859.89 | 35145.45 | 42257.41 | 35988.96 | 28525.76 | 24229.36 | 4339.67 | 221394.215
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($319,000) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54767.46 | 59123.34 | 45623.64 | 52101.56 | 33517.37 | 16235.31 | 319649.495
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2000-01 (94.7 BIL Btus) | 0 | 0 | 0 | 468000 | 6354800 | 12605900 | 19682500 | 15766350 | 15803900 | 13307450 | 8176900 | 2535700 | 94701500
2001-02 (84.2 BIL Btus) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13970210 | 14639200 | 11545805 | 13693100 | 8430600 | 4174700 | 84178915
2002-03 (91.3 BIL Btus) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($326,532) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54182.28 | 59123.34 | 51217.99 | 52101.56 | 35390.55 | 16235.31 | 326531.845
2002-03 ($432,450) | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78

## BTU Chart
3 YEAR BTU/COST COMPARISON

## Heating Degree Days
[15 empty] | 00/01 | 01/02 | 02/03 | 10 Year Avg.
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01 | 01/02 | 10 Year Avg.
[14 empty] | JUN | 64 | 63 | 35 | 54
JUN | 25 | 48 | 38 | 29 | 6 | 30 | 30 | 10 | 80 | 68 | 64 | 63 | 41.8 | JUL | 14 | 9 | 0 | 7.6667
JUL | 3 | 46 | 12 | 0 | 0 | 2 | 0 | 21 | 0 | 0 | 14 | 9 | 5.8 | AUG | 1 | 5 | 4 | 3.3333
AUG | 1 | 79 | 21 | 2 | 0 | 0 | 0 | 29 | 1 | 5 | 1 | 5 | 6.4 | SEP | 152 | 183 | 132 | 155.6667
SEP | 86 | 339 | 114 | 226 | 88 | 188 | 123 | 97 | 67 | 177 | 152 | 183 | 141.5 | OCT | 364 | 513 | 725 | 534
OCT | 425 | 668 | 493 | 462 | 336 | 485 | 438 | 465 | 465 | 489 | 364 | 513 | 451 | NOV | 1006 | 301 | 977 | 761.3333
NOV | 689 | 1300 | 927 | 910 | 743 | 1038 | 1100 | 1068 | 826 | 682 | 1006 | 301 | 860.1 | DEC | 1753 | 1148 | 1200 | 1367
DEC | 1502 | 1441 | 1255 | 1155 | 1155 | 1346 | 1399 | 1160 | 1208 | 1189 | 1753 | 1148 | 1276.8 | JAN | 1350 | 1234 | 1540 | 1374.6667
JAN | 1722 | 1405 | 1384 | 1692 | 1275 | 1596 | 1502 | 1338 | 1558 | 1498 | 1350 | 1234 | 1442.7 | FEB | 1440 | 1014 | 1372 | 1275.3333
FEB | 1254 | 1151 | 1466 | 1277 | 1090 | 1275 | 1063 | 918 | 1033 | 1068 | 1440 | 1014 | 1164.4 | MAR | 1113 | 1239 | 1043 | 1131.6667
MAR | 1146 | 922 | 948 | 796 | 739 | 1155 | 945 | 1030 | 921 | 754 | 1113 | 1239 | 964 | APR | 504 | 615 | 529 | 549.3333
APR | 639 | 406 | 513 | 513 | 581 | 608 | 481 | 395 | 480 | 559 | 504 | 615 | 524.9 | MAY | 198 | 357 | 230 | 261.6667
MAY | 303 | 110 | 155 | 155 | 126 | 200 | 216 | 58 | 167 | 180 | 198 | 357 | 181.2
| 7795 | 7915 | 7326 | 7217 | 6139 | 7923 | 7297 | 6589 | 6806 | 6669 | 7959 | 6681

## Cooling Degree Days
MACALESTER COLLEGE ACTUAL READINGS
COOLING DEGREE DAYS
| 89/90 | 90/91 | 91/92 | 92/93 | 93/94 | 94-95 | 95-96 | 96-97 | 97-98 (690) | 98-99 (750) | 99-00 (740) | 00/01 (612) | 01/02 ( 851) | 02/03 (859) | TOTAL
JUN | 101 | 285 | 116 | 182 | 111 | 287 | 306 | 233 | 192 | 113 | 135 | 106 | 175 | 199 | 185.7
JUL | 291 | 343 | 108 | 166 | 259 | 266 | 328 | 269 | 215 | 259 | 348 | 243 | 309 | 348 | 284.4
AUG | 130 | 308 | 84 | 138 | 251 | 176 | 289 | 334 | 131 | 210 | 160 | 160 | 267 | 172 | 215
SEP | 12 | 166 | 7 | 32 | 9 | 101 | 72 | 104 | 34 | 125 | 54 | 49 | 44 | 115 | 70.7
OCT | 2 | 0 | 0 | 6 | 1 | 0 | 8 | 0 | 27 | 0 | 0 | 5 | 1 | 0 | 4.2
NOV | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FEB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APR | 3 | 0 | 16 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 8 | 20 | 11 | 4.7
MAY | 17 | 18 | 110 | 25 | 7 | 29 | 35 | 21 | 90 | 43 | 43 | 41 | 35 | 14 | 35.8
TOTAL | 556 | 1121 | 441 | 549 | 645 | 859 | 1038 | 961 | 690 | 750 | 740 | 612 | 851 | 859 | 800.5

## Past Data
| ACTUAL | BTUs | TOTAL | FUEL |  | TOTAL | ELECT | TOTAL | TOTAL | TOTAL | BTU | COST
YEAR | HEATING | CONSUMED | FUEL | COST | KWH | ELECTRIC | COST | SQUARE | BTU | BTU | CONSUMP | per
| DEGREE | x1,000,000 | COST | per | CONSUMED | COST | per | FEET | CONSUM | COST | per FOOT | x1000k
| DAYS |  |  | 100k BTU |  |  | KWH |  | (x1000k) |  |  | BTUs
84-85 | 7632 | 100514 | 401058 | 0.39901 | 8767200 | 364038 | 0.041523 | 846365 | 130427.6864 | 765096 | 154103.3554 | 5.8661
85-86 | 7852 | 91852 | 328917 | 0.35809 | 8611200 | 361161 | 0.041941 | 846365 | 121233.4144 | 690078 | 143240.1085 | 5.6921
86-87 | 6238 | 86956 | 186058 | 0.21397 | 8407200 | 330664 | 0.039331 | 846365 | 115641.3664 | 516722 | 136632.9732 | 4.4683
87-88 | 7138 | 98071 | 235637 | 0.24027 | 8894600 | 376025 | 0.042276 | 846865 | 128419.3752 | 611662 | 151640.9052 | 4.763
88-89 (1) | 7817 | 100426 | 231792 | 0.23081 | 9900000 | 418470 | 0.04227 | 846365 | 134204.8 | 650262 | 158566.1033 | 4.8453
89-90 (2) | 8181 | 99062 | 232017 | 0.23421 | 9614400 | 431765 | 0.044908 | 938865 | 131866.3328 | 663782 | 140452.9222 | 5.0337
90-91 (3) | 7795 | 98739 | 251671 | 0.25489 | 10459200 | 463053 | 0.044272 | 944865 | 134425.7904 | 714724 | 142269.8379 | 5.3169
91-92 | 7915 | 92268 | 159770 | 0.17316 | 10699200 | 473973 | 0.0443 | 944865 | 128773.6704 | 633743 | 136287.904 | 4.9214
92-93 (4) | 7296 | 95977 | 165834.46 | 0.17279 | 10420800 | 480192 | 0.044 | 966865 | 131532.7696 | 646026.46 | 136040.4706 | 4.9115
93-94 (5) | 7098 | 85173 | 212107.05 | 0.24903 | 10384173 | 487721.55 | 0.046968 | 972865 | 120603.7983 | 699828.6 | 123967.6608 | 5.8027
94-95 | 6139 | 77444 | 155666.62 | 0.20101 | 10454200 | 509883.07 | 0.048773 | 972865 | 113113.7304 | 665550 | 116268.6811 | 5.8839
95-96 (6) | 7921 | 91589 | 211776 | 0.23122 | 10836825 | 531950.66 | 0.049087 | 972865 | 128564.2469 | 743726 | 132149 | 5.7849
96-97 (7) | 7297 | 99991 | 293146.26 | 0.29317 | 11983679 | 559179.31 | 0.046662 | 1018615 | 140879.3127 | 852325.57 | 139404 | 5.8647
97-98 (8) | 6589 | 82412 | 223641.54 | 0.27137 | 12782400 | 613894 | 0.048027 | 1056615 | 126025.5488 | 837535.54 | 119272.9128 | 6.6458
98-99 | 6788 | 86690 | 197452.77 | 0.22777 | 12972000 | 626697 | 0.048312 | 1056615 | 130950.464 | 824149.77 | 123933.9438 | 6.2936
99-00 (9) | 6669 | 76959 | 221394 | 0.28768 | 12117600 | 621699 | 0.051305 | 1053903 | 118370 | 843093 | 112315.8393 | 7.1225
00-01 (10) | 7959 | 94701 | 506962 | 0.53533 | 11611968 | 567550.07 | 0.048876 | 1149717 | 134321.0348 | 1074512.07 | 116829.6501 | 7.9996
01-02 (11) | 6681 | 85416 | 326532 | 0.38228 | 12739200 | 640022.43 | 0.05024 | 1187717 | 128882.1504 | 966554.43 | 108512.5079 | 7.4995
02-03 | 7787 | 91334 | 432449.78 | 0.47348 | 13257600 | 637913.79 | 0.048117 | 1187717 | 136568.9312 | 1070363.57 | 114984.4039 | 7.8375
1. Library built and on line.
2. Weyerhaeuser Hall renovated--a/c added.
3. Carnegie Hall renovated--a/c added along with more usable area.
4. Humanities renovated--additional space and a/c.
5. Old Main renovated-additional space and a/c.
6. Rice renovation under way--construction heat throughout the year.
7. Rice operational with new mechanical systems, Olin's construction heat supplied by gas kiln meter--not reflected in this report.
8. New Residence Hall put on-line in August 1997. Additional 38,000 square feet of area. First air conditioned residence hall.
9. Old Dayton Hall and Student Union torn down summer of 1999. Temporary heat for Campus Center Construction.
10. Kagin taken out of operation during January 2001. Campus Center comes on line in January.
11. Kagin comes back on line January 2002.

## 0203 Budget
MACALESTER COLLEGE
MONTHLY ENERGY BUDGET REPORT
JUNE 2002 - MAY 2003
|  |  | BUDGETED | BUDGETED | ESTIMATED | ESTIMATED
ENERGY | QUANTITY |  | CONSUMPTION | TOTAL | TOTAL | TOTAL
TYPE | CONSUMED | EXPENDITURE | (BTUs/KWH) | EXPENDITURE | CONSUMPTION | EXPENDITURE
| 2002-06-01 | 2002-06-01 | 2002-06-01 | 2002-06-01 | 2002-06-01 | 2002-06-01
| 2003-05-31 | 2003-05-31 | 2003-05-31 | 2003-05-31 | 2003-05-31 | 2003-05-31
GAS (CCF) | 389420 | 195060.3 |  |  | 389420 | 195060.3
OIL (GAL.)
#6 | 349283 | 237389.48 |  |  | 349283 | 237389.48
#2 | 0 | 0 |  |  | 0 | 0
TOTAL BTUs | 91334450 | 432449.78 | 100000000 | 513500 | 91334450 | 432449.78
(* 1,000)
ELEC. (KWH) | 13257600 | 637913.79 | 15745000 | 787250 | 13257600 | 637913.79
TOTAL
EXPENDED | 136569381.2 | 1070363.57 | 153721940 | 1300750 | 136569381.2 | 1070363.57
Variance:
|  |  |  | Budget -vs- Estimate |  | 230386.43
Fuel Variance:
|  |  |  | Consumption |  | -44497.5992
|  |  |  | Price |  | -36552.6207
|  |  |  | Sub-Total |  | -81050.22
Electrical Variance:
|  |  |  | Consumption |  | -124370
|  |  |  | Price |  | -24966.21
|  |  |  | Sub-Total |  | -149336.21
Total Variance
|  |  |  | Fuel & Electrical |  | -230386.43

## HDD vs Consump Stats
YEAR | HEATING | CONSUMED | FUEL | COST | KWH | ELECTRIC | COST | SQUARE | BTU | BTU | CONSUMP | per
| HDD | x1,000,000 | COST | PER | CONSUMED | COST | PER | FEET | CONSUM | COST | BTU | X1000K
90-91(3) | 7795 | 98739 | 251671 | 0.25489 | 10459200 | 463053 | 0.044272 | 944865 | 134425.7904 | 714724 | 142269.8379 | 5.3169
91-92 | 7915 | 92268 | 159770 | 0.17316 | 10699200 | 473973 | 0.0443 | 944865 | 128773.6704 | 633743 | 136287.904 | 4.9214
92-93(4) | 7296 | 95977 | 165834.46 | 0.17279 | 10420800 | 480192 | 0.044 | 966865 | 131532.7696 | 646026.46 | 136040.4706 | 4.9115
93-94(5) | 7098 | 85173 | 212107.05 | 0.24903 | 10384173 | 487721.55 | 0.046968 | 972865 | 120603.7983 | 699828.6 | 123967.6608 | 5.8027
94-95 | 6139 | 77444 | 155666.62 | 0.20101 | 10454200 | 509883.07 | 0.048773 | 972865 | 113140 | 665550 | 116295.6834 | 5.8825
95-96(6) | 7921 | 91589 | 211776 | 0.23122 | 10836825 | 531950.66 | 0.049 | 972865 | 128564 | 743726 | 132149 | 5.7849
96-97(7) | 7297 | 99991 | 293146.26 | 0.29317 | 11983679 | 559179.31 | 0.049 | 1018615 | 140880 | 852325.57 | 139404 | 5.8647
97-98(8) | 6589 | 82412 | 223641.54 | 0.27137 | 12782400 | 613894 | 0.048 | 1056615 | 120632 | 837535.54 | 114168.3584 | 6.9429
98-99 | 6806 | 86670 | 199452 | 0.23013 | 12972000 | 626697 | 0.048 | 1056615 | 131330 | 826149 | 124293.1437 | 6.2906
99-00(9) | 6698 | 77025 | 221699 | 0.28783 | 12117600 | 621699 | 0.051305 | 1053903 | 118370 | 843398 | 112315.8393 | 7.1251
00-01 (10) | 7959 | 94701 | 506962 | 0.53533 | 11611968 | 567550.07 | 0.048876 | 1149717 | 134321.0348 | 1074512.07 | 116829.6501 | 7.9996
01-02 (11) | 6681 | 85416 | 326532 | 0.38228 | 12739200 | 640022.43 | 0.05024 | 1187717 | 128882.1504 | 966554.43 | 108512.5079 | 7.4995
02-03 | 7787 | 91334 | 432449.78 | 0.47348 | 13257600 | 637913.79 | 0.048117 | 1187717 | 136568.9312 | 1070363.57 | 114984.4039 | 7.8375
YEAR | HEATING | CONSUMED | FUEL
| HDD | x1,000,000 | COST
90-91 | 7795 | 9873.9 | 25167.1
91-92 | 7915 | 9226.8 | 15977
92-93 | 7296 | 9597.7 | 16583.446
93-94 | 7098 | 8517.3 | 21210.705
94-95 | 6139 | 7744.4 | 15566.662
95-96 | 7921 | 9158.9 | 21177.6
96-97 | 7297 | 9999.1 | 29314.626
97-98 | 6589 | 8241.2 | 22364.154
98-99 | 6788 | 8667 | 19945.2
99-00 | 6669 | 7702.5 | 22169.9
00-01 | 7959 | 9470 | 50696
01-02 | 6681 | 8542 | 32653
02-03 | 7787 | 9133 | 43245

## Condensate by Bldg
METER READINGS
|  | June |  | July |  | August |  | September |  | October |  | November |  | December |  | January |  | February |  | March |  | April |  | May | Annual
| 2002-06-04 |  | 2002-08-02 |  | 2002-09-03 |  | 2002-10-01 |  | 2002-11-06 |  | 2002-12-03 |  | 2003-01-03 |  | 2003-02-03 |  | 2003-03-03 |  | 2003-04-02 |  | 2003-05-01 |  | 2003-06-03 |  |  | %
| READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | TOTAL
ART & POWER PLANT | 3085500 | 0 | 0 | 0 | 0 | 0 | 3090770 | 5270 | 3137190 | 46420 | 3185880 | 48690 | 3242050 | 56170 | 3293930 | 51880 | 3346250 | 52320 | 3395330 | 49080 | 3431620 | 36290 | 3443970 | 12350 | 309390 | 4.861%
CAMPUS CENTER | 1116760 | 0 | 0 | 0 | 0 | 0 | 1133640 | 16880 | 1265590 | 131950 | 1371690 | 106100 | 1476620 | 104930 | 1607830 | 131210 | 1735350 | 127520 | 1834250 | 98900 | 1912620 | 78370 | 1946350 | 33730 | 730690 | 11.48%
CARNEGIE | 857810 | 0 | 0 | 0 | 0 | 0 | 859590 | 1780 | 879400 | 19810 | 899560 | 20160 | 924780 | 25220 | 962790 | 38010 | 994040 | 31250 | 1014620 | 20580 | 1025960 | 11340 | 1029850 | 3890 | 151460 | 2.38%
CHAPEL | 111330 | 0 | 0 | 0 | 0 | 0 | 114080 | 2750 | 131520 | 17440 | 147710 | 16190 | 169750 | 22040 | 199140 | 29390 | 222970 | 23830 | 239460 | 16490 | 252070 | 12610 | 254770 | 2700 | 126950 | 1.995%
FIELDHOUSE | 5704810 | 0 | 0 | 0 | 0 | 0 | 5710830 | 6020 | 5762580 | 51750 | 5820730 | 58150 | 5892610 | 71880 | 5985770 | 93160 | 6062580 | 76810 | 6110570 | 47990 | 6134890 | 24320 | 6143780 | 8890 | 390980 | 6.143%
GYM | 171120 | 0 | 0 | 0 | 0 | 0 | 171120 | 0 | 171870 | 750 | 173530 | 1660 | 175650 | 2120 | 178290 | 2640 | 180400 | 2110 | 181450 | 1050 | 181810 | 360 | 181810 | 0 | 9640 | 0.1515%
HUMANITIES | 4259410 | 0 | 0 | 0 | 0 | 0 | 4262170 | 2760 | 4286890 | 24720 | 4311990 | 25100 | 4347750 | 35760 | 4396610 | 48860 | 4439490 | 42880 | 4469750 | 30260 | 4486500 | 16750 | 4494070 | 7570 | 204400 | 3.212%
KAGIN | 963760 | 0 | 0 | 0 | 0 | 0 | 963820 | 60 | 977550 | 13730 | 997940 | 20390 | 1022840 | 24900 | 1022840 | 0 | 1022840 | 0 | 1022840 | 0 | 1022840 | 0 | 1022840 | 0 | 59080 | 0.9283%
LIBRARY | 771500 | 0 | 0 | 0 | 0 | 0 | 774750 | 3250 | 804390 | 29640 | 830770 | 26380 | 863890 | 33120 | 907120 | 43230 | 947290 | 40170 | 979030 | 31740 | 1002930 | 23900 | 1014460 | 11530 | 211220 | 3.319%
MUSIC | 332600 | 0 | 0 | 0 | 0 | 0 | 333940 | 1340 | 352690 | 18750 | 371100 | 18410 | 399000 | 27900 | 445950 | 46950 | 487560 | 41610 | 512080 | 24520 | 523810 | 11730 | 525970 | 2160 | 168850 | 2.653%
OLD MAIN | 709230 | 0 | 0 | 0 | 0 | 0 | 710160 | 930 | 717040 | 6880 | 723270 | 6230 | 730140 | 6870 | 746490 | 16350 | 765640 | 19150 | 776350 | 10710 | 780790 | 4440 | 782700 | 1910 | 62760 | 0.9861%
GD DAYTON | 937200 | 0 | 0 | 0 | 0 | 0 | 939900 | 2700 | 960000 | 20100 | 979500 | 19500 | 1003800 | 24300 | 1039200 | 35400 | 1071000 | 31800 | 1096700 | 25700 | 1114800 | 18100 | 1122200 | 7400 | 159300 | 2.503%
POOL | 4513890 | 0 | 0 | 0 | 0 | 0 | 4517290 | 3400 | 4538840 | 21550 | 4558830 | 19990 | 4569440 | 10610 | 4579000 | 9560 | 4585880 | 6880 | 4591650 | 5770 | 4595590 | 3940 | 4597050 | 1460 | 77390 | 1.216%
RICE | 10787100 | 0 | 0 | 0 | 0 | 0 | 10808300 | 21200 | 11015700 | 207400 | 11225700 | 210000 | 11491300 | 265600 | 11827500 | 336200 | 12128900 | 301400 | 12343200 | 214300 | 12468900 | 125700 | 12515400 | 46500 | 1514000 | 23.79%
THEATER | 3756630 | 0 | 0 | 0 | 0 | 0 | 3767440 | 10810 | 3826780 | 59340 | 3887190 | 60410 | 3960410 | 73220 | 4057100 | 96690 | 4142890 | 85790 | 4209600 | 66710 | 4266420 | 56820 | 4295160 | 28740 | 471820 | 7.413%
WEYERHAEUSER HALL | 748510 | 0 | 0 | 0 | 0 | 0 | 751050 | 2540 | 763890 | 12840 | 771310 | 7420 | 776880 | 5570 | 784390 | 7510 | 790990 | 6600 | 802220 | 11230 | 812260 | 10040 | 818840 | 6580 | 59100 | 0.9286%
BIGELOW | 1181200 | 0 | 0 | 0 | 0 | 0 | 1184180 | 2980 | 1206920 | 22740 | 1228550 | 21630 | 1259770 | 31220 | 1303120 | 43350 | 1346260 | 43140 | 1380420 | 34160 | 1399920 | 19500 | 1407350 | 7430 | 191990 | 3.017%
DOTY | 3213030 | 0 | 0 | 0 | 0 | 0 | 3220940 | 7910 | 3281180 | 60240 | 3339720 | 58540 | 3413140 | 73420 | 3507070 | 93930 | 3587880 | 80810 | 3653860 | 65980 | 3697520 | 43660 | 3700080 | 2560 | 421070 | 6.616%
DUPRE | 2695370 | 0 | 0 | 0 | 0 | 0 | 2702140 | 6770 | 2769590 | 67450 | 2839100 | 69510 | 2932830 | 93730 | 3055690 | 122860 | 3161190 | 105500 | 3234540 | 73350 | 3279910 | 45370 | 3294350 | 14440 | 525630 | 8.259%
KIRK | 4659590 | 0 | 0 | 0 | 0 | 0 | 4660140 | 550 | 4662240 | 2100 | 4664190 | 1950 | 4666440 | 2250 | 4669490 | 3050 | 4672040 | 2550 | 4678250 | 6210 | 4690830 | 12580 | 4694500 | 3670 | 28700 | 0.4509%
TURCK | 802120 | 0 | 0 | 0 | 0 | 0 | 811010 | 8890 | 854420 | 43410 | 888960 | 34540 | 917620 | 28660 | 951530 | 33910 | 987340 | 35810 | 1016940 | 29600 | 1041420 | 24480 | 1049400 | 7980 | 217680 | 3.42%
WALLACE & 30 MAC | 5697720 | 0 | 0 | 0 | 0 | 0 | 5701390 | 3670 | 5735110 | 33720 | 5762900 | 27790 | 5792300 | 29400 | 5821030 | 28730 | 5838080 | 17050 | 5844480 | 6400 | 5849030 | 4550 | 5850270 | 1240 | 146150 | 2.296%
DISTRICT HEATING | 2321190 | 0 | 0 | 0 | 0 | 0 | 2322190 | 1000 | 2335350 | 13160 | 2351690 | 16340 | 2373770 | 22080 | 2406830 | 33060 | 2434830 | 28000 | 2452290 | 17460 | 2461870 | 9580 | 2464820 | 2950 | 126170 | 1.982%
|  | 0 |  | 0 |  | 0 |  | 113460 |  | 925890 |  | 895080 |  | 1070970 |  | 1345930 |  | 1202980 |  | 888190 |  | 594430 |  | 215680 | 6364420 | 100%

## Electrical Read by Bldg
LOCATION | May | JUNE |  | JULY |  | AUGUST |  | SEPTEMER |  | OCTOBER |  | NOVEMBER |  | DECEMBER |  | JANUARY |  | FEBRUARY |  | MARCH |  | APRIL |  | MAY |  | ANNUAL | % OF
READ DATE |  | 2002-07-02 |  | Estimated |  | 2002-09-03 |  | 2002-10-01 |  | 2002-11-06 |  | 2002-12-03 |  | 2003-01-05 |  | 2003-02-03 |  | 2003-03-03 |  | 2003-04-02 |  | 2003-05-01 |  | 2003-06-03
| Reading | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | TOTAL | CAMPUS
CAMPUS CENTER | 61265.3 | 51321.4 | 90056.1 | 68947.3 | 117625.9 | 67170 | 98222.7 | 87428.7 | 120258.7 | 40058 | 52629.3 | 54884.4 | 114826.4 | 65206.7 | 110322.3 | 86586.1 | 121379.4 | 18530.9 | 31944.8 | 47600 | 229069.1 | 71700 | 124100 | 80786.7 | 109086.7 | 1319521.4 | 10.08%
ART LIGHTS (TC) | 91187 | 91777 | 11800 | 92625 | 16960 | 93318 | 13860 | 94342 | 20480 | 96043 | 34020 | 97271 | 24560 | 98636 | 27300 | 99955 | 26380 | 1321 | 27320 | 2733 | 28240 | 4111 | 27560 | 5217 | 22120 | 280600 | 2.145%
POWER PLANT | 137 | 821 | 20520 | 1740 | 27570 | 2381 | 19230 | 2937 | 16680 | 3681 | 22320 | 4198 | 15510 | 4747 | 16470 | 5613 | 25980 | 6407 | 23820 | 7147 | 22200 | 7790 | 19290 | 8419 | 18870 | 248460 | 1.899%
CHAPEL | 98957 | 99282 | 9750 | 99907 | 18750 | 409 | 15060 | 859 | 13500 | 1237 | 11340 | 1548 | 9330 | 2002 | 13620 | 2482 | 14400 | 2908 | 12780 | 3333 | 12750 | 3719 | 11580 | 4019 | 9000 | 151860 | 1.161%
CARNEGIE | 68620 | 69140 | 15600 | 69783 | 19290 | 70262 | 14370 | 70993 | 21930 | 71959 | 28980 | 72676 | 21510 | 73378 | 21060 | 74122 | 22320 | 75036 | 27420 | 75909 | 26190 | 76708 | 23970 | 77418 | 21300 | 263940 | 2.017%
FIELDHOUSE | 91299 | 92128 | 24870 | 93302 | 35220 | 94283 | 29430 | 95336 | 31590 | 96556 | 36600 | 97452 | 26880 | 98346 | 26820 | 99525 | 35370 | 985 | 43800 | 2392 | 42210 | 3462 | 32100 | 4454 | 29760 | 394650 | 3.016%
GYM-POOL | 38944 | 39517 | 57300 | 40251 | 73400 | 40870 | 61900 | 41522 | 65200 | 42362 | 84000 | 42976 | 61400 | 43598 | 62200 | 44307 | 70900 | 44970 | 66300 | 45657 | 68700 | 46321 | 66400 | 47047 | 72600 | 810300 | 6.193%
HUM POW & LIG | 20025 | 20838 | 24390 | 21777 | 28170 | 22587 | 24300 | 23541 | 28620 | 24758 | 36510 | 25627 | 26070 | 26502 | 26250 | 27457 | 28650 | 28466 | 30270 | 29491 | 30750 | 30548 | 31710 | 31596 | 31440 | 347130 | 2.653%
KAGIN | 3437 | 344.7 | 96907.7 | 345 | 100000.3 | 345.5 | 100000.5 | 346 | 100000.5 | 346.3 | 100000.3 | 2055.1 | 101708.8 | 4406.9 | 102351.8 | 7195.6 | 102788.7 | 9986.2 | 102790.6 | 12883.5 | 102897.3 | 15723 | 102839.5 | 18594.1 | 102871.1 | 1215157.1 | 9.287%
30 MAC | 94883 | 95609 | 5445 | 96505 | 6720 | 97329 | 6180 | 98558 | 9217.5 | 257 | 12742.5 | 1510 | 9397.5 | 2705 | 8962.5 | 3841 | 8520 | 5192 | 10132.5 | 6609 | 10627.5 | 8067 | 10935 | 9310 | 9322.5 | 108202.5 | 0.8269%
LIBRARY | 4184 | 4381 | 63040 | 4674 | 93760 | 4905 | 73920 | 5199 | 94080 | 5567 | 117760 | 5825 | 82560 | 6080 | 81600 | 6345 | 84800 | 6664 | 102080 | 6970 | 97920 | 7259 | 92480 | 7507 | 79360 | 1063360 | 8.127%
MUSIC (PB1) | 39719 | 40607 | 17760 | 41542 | 18700 | 42382 | 16800 | 43567 | 23700 | 45119 | 31040 | 46154 | 20700 | 47143 | 19780 | 48597 | 29080 | 49872 | 25500 | 51072 | 24000 | 52243 | 23420 | 53288 | 20900 | 271380 | 2.074%
MUSIC LIGHTS (TB) | 14742 | 15077 | 6700 | 15490 | 8260 | 15852 | 7240 | 16281 | 8580 | 16871 | 11800 | 17315 | 8880 | 17785 | 9400 | 18312 | 10540 | 18829 | 10340 | 19328 | 9980 | 19834 | 10120 | 20282 | 8960 | 110800 | 0.8468%
OLD MAIN | 47048 | 47764 | 14320 | 48619 | 17100 | 49335 | 14320 | 50254 | 18380 | 51516 | 25240 | 52421 | 18100 | 53405 | 19680 | 54646 | 24820 | 56020 | 27480 | 57357 | 26740 | 58404 | 20940 | 59312 | 18160 | 245280 | 1.875%
GD DAYTON | 1979269 | 2002881 | 23612 | 2033016 | 30135 | 2058263 | 25247 | not working | 0 | not working | 0 | 2136665 | 78402 | 2164817 | 28152 | 2198405 | 33588 | 2248121 | 49716 | 2295963 | 47842 | 2326547 | 30584 | 2355148 | 28601 | 375879 | 2.873%
RICE | 13996766 | 14168548 | 171782 | 14397803 | 229255 | 14586161 | 188358 | 14775849 | 189688 | 14999812 | 223963 | 15164659 | 164847 | 15341551 | 176892 | 15520486 | 178935 | 15698028 | 177542 | 15882805 | 184777 | 16072933 | 190128 | 16274563 | 201630 | 2277797 | 17.41%
THEATER (TA) | 60177 | 60722 | 10900 | 61348 | 12520 | 61857 | 10180 | 62791 | 18680 | 64531 | 34800 | 65770 | 24780 | 67072 | 26040 | 68462 | 27800 | 70066 | 32080 | 71545 | 29580 | 72967 | 28440 | 74104 | 22740 | 278540 | 2.129%
WEY HALL | 4400 | 4882 | 9640 | 5498 | 12320 | 6007 | 10180 | 6560 | 11060 | 7292 | 14640 | 7780 | 9760 | 8286 | 10120 | 8926 | 12800 | 9625 | 13980 | 10347 | 14440 | 10913 | 11320 | 11532 | 12380 | 142640 | 1.09%
HEALTH CENTER | 84159 | 84459 | 2250 | 84926 | 3502.5 | 85363 | 3277.5 | 85750 | 2902.5 | 86074 | 2430 | 86291 | 1627.5 | 86493 | 1515 | 86769 | 2070 | 87221 | 3390 | 87670 | 3367.5 | 87896 | 1695 | 88107 | 1582.5 | 29610 | 0.2263%
BIGELOW | 62383 | 62755 | 22320 | 63248 | 29580 | 63530 | 16920 | 63926 | 23760 | 64476 | 33000 | 64871 | 23700 | 65240 | 22140 | 65668 | 25680 | 66278 | 36600 | 66885 | 36420 | 67313 | 25680 | 67656 | 20580 | 316380 | 2.418%
DOTY | 85593 | 86453 | 25800 | 87188 | 22050 | 87944 | 22680 | 89078 | 34020 | 90254 | 35280 | 91112 | 25740 | 91887 | 23250 | 92658 | 23130 | 93589 | 27930 | 94513 | 27720 | 95452 | 28170 | 96189 | 22110 | 317880 | 2.429%
DUPRE | 1844 | 184.4 | 98340.4 | 184.4 | 100000 | 189.1 | 100004.7 | 222.4 | 100033.3 | 261.6 | 100039.2 | 3293.7 | 103032.1 | 7002.8 | 103709.1 | 10479.8 | 103477 | 14941.6 | 104461.8 | 19417.8 | 104476.2 | 23844.7 | 104426.9 | 27578.5 | 103733.8 | 1225734.5 | 9.368%
KIRK | 123 | 157 | 5440 | 219 | 9920 | 258 | 6240 | 373 | 18400 | 536 | 26080 | 683 | 23520 | 827 | 23040 | 988 | 25760 | 1165 | 28320 | 1315 | 24000 | 1438 | 19680 | 1536 | 15680 | 226080 | 1.728%
TURCK | 54306 | 54670 | 5460 | 55151 | 7215 | 55571 | 6300 | 56533 | 14430 | 57742 | 18135 | 58612 | 13050 | 59330 | 10770 | 59955 | 9375 | 60881 | 13890 | 61814 | 13995 | 62796 | 14730 | 63492 | 10440 | 137790 | 1.053%
STADIUM | 7667 | 7759 | 9200 | 7948 | 18900 | 8097 | 14900 | 8311 | 21400 | 9148 | 83700 | 9880 | 73200 | 10806 | 92600 | 12053 | 124700 | 13116 | 106300 | 13857 | 74100 | 14234 | 37700 | 14408 | 17400 | 674100 | 5.152%
WALLACE | 85384 | 85920 | 4020 | 86732 | 6090 | 87722 | 7425 | 89890 | 16260 | 92410 | 18900 | 94246 | 13770 | 95989 | 13072.5 | 97476 | 11152.5 | 99404 | 14460 | 1317 | 14347.5 | 3252 | 14512.5 | 4301 | 7867.5 | 141877.5 | 1.084%
CHILLER | 5485.16 | 5732.45 | 9891.6 | 6118.28 | 15433.2 | 6351.27 | 9319.6 | 6519.84 | 6742.8 | 6531.74 | 476 | 6531.74 | 0 | 6531.74 | 0 | 6531.74 | 0 | 6531.91 | 6.8 | 6531.91 | 0 | 6568.09 | 1447.2 | 6655.69 | 3504 | 46821.2 | 0.3578%
CHAPEL CHILLER | 44488 | 44627 | 5560 | 45341 | 28560 | 45735 | 15760 | 45837 | 4080 | 45870 | 1320 | 45894 | 960 | 45922 | 1120 | 45952 | 1200 | 45978 | 1040 | 46005 | 1080 | 46030 | 1000 | 46059 | 1160 | 62840 | 0.4803%
SUBTOTAL |  |  | 862674.8 |  | 1107006.9 |  | 931625 |  | 1033673.3 |  | 1197745.3 |  | 1097821.3 |  | 1078237.2 |  | 1185595.6 |  | 1151694.5 |  | 1308419.1 |  | 1106958.1 |  | 1023159.1 | 13084610.2 | 1
MAIN METER |  |  | 1056000 |  | 1262400 |  | 1020000 |  | 1329600 |  | 998400 |  | 1291200 |  | 854400 |  | 1128000 |  | 1240800 |  | 976800 |  | 1101600 |  | 998400 | 13257600
% OF MAIN METER |  |  | 81.69% |  | 87.69% |  | 91.34% |  | 77.74% |  | 120% |  | 85.02% |  | 126.2% |  | 105.1% |  | 92.82% |  | 133.9% |  | 100.5% |  | 102.5% | 98.7%