## OpRpt
Main Meters
|  |  | Month: | February | Year: | 2003
Total Steam Flow (Lbs) From Meter |  |  |  | 14626000 | x 884 Btus |  |  | 12929384000 | Btus
FUEL:
|  | GAS (Xcel) |  | 1449 | Therms x 100,000 |  |  | 144900000 | Btus
|  | #6 Oil (Marathon) |  | 102128 | Gallons x 150,000 |  |  | 15319200000 | Btus
|  | #2 Oil |  |  | Gallons x 138,000 |  |  | 0 | Btus
|  |  | TOTAL MONTHLY FUEL CONSUMPTION = |  |  |  |  | 15464100000 | Btus
|  | GAS | HP Meter | 47 | MCF x 1,000,000 |  |  | 47000000 | Btus
|  | #6 Oil HP Reading |  | 101888 | Gallons x 150,000 |  |  | 15283200000 | Btus
BOILER EFFICIENCY:
|  | Btu In Steam / Btu In Fuel = | [5 empty] | 83.61%
MAKE-UP WATER:
|  |  | 113800 | Gallons x 8.33 |  |  |  | 947954 | lbs
|  |  |  | [(Gallons/7.48cuft)/100] |  |  |  | 152.139 | 100 cu.ft.
|  | LBS Make-Up Water / LBS Steam = | [5 empty] | 6.481% | Make-Up Water
BOILER OPERATIONAL COSTS (EXCLUSIVE OF ELECTRICITY)
|  | GAS (Xcel) |  | 1449 | Therm x | 0.85448 |  | 1238.1369
|  | #6 Oil (Marathon) |  | 102128 | Gallon x | 0.6911 |  | 70580.6608
|  | #2 Fuel Oil |  |  | Gallon x |  |  | 0
|  | Water |  | 152.14 | 100cuft x | 3.89 |  | 591.8246
|  | Chem 938 |  | 10 | Gallon x | 13.52 |  | 135.2
|  |  | 960 | 4.5 | Pound x | 1.36 |  | 6.12
|  |  | 8588 | 12 | Gallon x | 14.49 |  | 173.88
|  |  | 9010 | 2 | Gallon x | 14.1 |  | 28.2
|  |  |  | TOTAL COST: |  |  |  | 72754.0223
| COST PER 1,000 LBS OF STEAM: | [6 empty] | 4.56
ELECTRICITY USED:
|  | Xcel reading |  | 1240800 | Kwh x | 0.041885 | = | 51970.908
|  | HP reading |  | 1130079 | Kwh x | 0.041885 | = | 47333.3589
MONTHLY TEMPERATURES:
|  |  | Period High |  | 47 | ˚ F
|  |  | Period Low |  | -14 | ˚ F
|  |  | Ave. High |  | 24.3 | ˚ F
|  |  | Ave. Low |  | 6.8 | ˚ F
|  |  | Period Mean Temperature |  | 16 | ˚ F
DEGREE DAYS:
| Heating Degree Days |  |  | 1372 |  | Cooling Degree Days |  |  | 0
CHILLER RUN TIME:
| New # 1 |  | 0 | Hours
| Old # 2 |  | 0 | Hours
| Chapel |  | 0 | Hours

## MgmtRpt
[5 empty] | MONTHLY MANAGEMENT REPORT | [5 empty] | MONTH: |  |  | YEAR:
DATE | CHILLER |  | HOUR |  | BOILER |  | STEAM FLOW X 1000 | GAS MCE | OIL | GAL | WATER GAL | ELECTRIC KWH |  | TEMP |  | DEG DAY
| 1 | 2 | 3 | 1 | 2 | 3 |  |  | #6 | #2 |  |  | HI | LO | AVG
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
AVG
TOTAL