## OpRpt
Main Meter
|  |  | Month: | November | Year: | 2002
Total Steam Flow (Lbs) From Meter |  |  |  | 9980000 | x 884 Btus |  |  | 8822320000 | Btus
FUEL:
|  | GAS (Xcel) |  | 118973 | Therms x 100,000 |  |  | 11897300000 | Btus
|  | #6 Oil (Marathon) |  |  | Gallons x 150,000 |  |  | 0 | Btus
|  | #2 Oil |  |  | Gallons x 138,000 |  |  | 0 | Btus
|  |  | TOTAL MONTHLY FUEL CONSUMPTION = |  |  |  |  | 11897300000 | Btus
|  | GAS | HP Meter | 11727 | MCF x 1,000,000 |  |  | 11727000000 | Btus
|  | #6 Oil HP Reading |  |  | Gallons x 150,000 |  |  | 0 | Btus
BOILER EFFICIENCY:
|  | Btu In Steam / Btu In Fuel = | [5 empty] | 74.15%
MAKE-UP WATER:
|  |  | 42760 | Gallons x 8.33 |  |  |  | 356190.8 | lbs
|  |  |  | [(Gallons/7.48cuft)/100] |  |  |  | 57.1658 | 100 cu.ft.
|  | LBS Make-Up Water / LBS Steam = | [5 empty] | 3.569% | Make-Up Water
BOILER OPERATIONAL COSTS (EXCLUSIVE OF ELECTRICITY)
|  | GAS (Xcel) |  | 118973 | Therm x | 0.48511 |  | 57714.6351
|  | #6 Oil (Marathon) |  |  | Gallon x |  |  | 0
|  | #2 Fuel Oil |  |  | Gallon x |  |  | 0
|  | Water |  | 57 | 100cuft x | 3.75 |  | 213.75
|  | Chem 938 |  | 7 | Gallon x | 13.52 |  | 94.64
|  |  | 960 | 2.5 | Pound x | 1.36 |  | 3.4
|  |  | 8540 | 10 | Gallon x | 14.49 |  | 144.9
|  |  | 9010 | 1 | Gallon x | 14.1 |  | 14.1
|  |  |  | TOTAL COST: |  |  |  | 58185.4251
| COST PER 1,000 LBS OF STEAM: | [6 empty] | 5.8302
ELECTRICITY USED:
|  | Xcel reading |  | 1291200 | Kwh x | 0.042427 | = | 54781.7424
|  | HP reading |  | 1061965 | Kwh x | 0.042427 | = | 45055.9891
MONTHLY TEMPERATURES:
|  |  | Period High |  | 65 | ˚ F
|  |  | Period Low |  | 16 | ˚ F
|  |  | Ave. High |  | 39.4 | ˚ F
|  |  | Ave. Low |  | 25.8 | ˚ F
|  |  | Period Mean Temperature |  | 31.5 | ˚ F
DEGREE DAYS:
| Heating Degree Days |  |  | 977 |  | Cooling Degree Days |  |  | 0
CHILLER RUN TIME:
| New # 1 |  | 0 | Hours
| Old # 2 |  | 0 | Hours
| Chapel |  | 0 | Hours

## MgmtRpt
[5 empty] | MONTHLY MANAGEMENT REPORT | [5 empty] | MONTH: |  |  | YEAR:
DATE | CHILLER |  | HOUR |  | BOILER |  | STEAM FLOW X 1000 | GAS MCE | OIL | GAL | WATER GAL | ELECTRIC KWH |  | TEMP |  | DEG DAY
| 1 | 2 | 3 | 1 | 2 | 3 |  |  | #6 | #2 |  |  | HI | LO | AVG
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
AVG
TOTAL