## OpRpt
Main Meters
|  |  | Month: | October | Year: | 2002
Total Steam Flow (Lbs) From Meter |  |  |  | 8481000 | x 884 Btus |  |  | 7497204000 | Btus
FUEL:
|  | GAS (Xcel) |  | 95874 | Therms x 100,000 |  |  | 9587400000 | Btus
|  | #6 Oil (Marathon) |  |  | Gallons x 150,000 |  |  | 0 | Btus
|  | #2 Oil |  |  | Gallons x 138,000 |  |  | 0 | Btus
|  |  | TOTAL MONTHLY FUEL CONSUMPTION = |  |  |  |  | 9587400000 | Btus
|  | GAS | HP Meter | 9369 | MCF x 1,000,000 |  |  | 9369000000 | Btus
|  | #6 Oil HP Reading |  |  | Gallons x 150,000 |  |  | 0 | Btus
BOILER EFFICIENCY:
|  | Btu In Steam / Btu In Fuel = | [5 empty] | 78.2%
MAKE-UP WATER:
|  |  | 29870 | Gallons x 8.33 |  |  |  | 248817.1 | lbs
|  |  |  | [(Gallons/7.48cuft)/100] |  |  |  | 39.9332 | 100 cu.ft.
|  | LBS Make-Up Water / LBS Steam = | [5 empty] | 2.934% | Make-Up Water
BOILER OPERATIONAL COSTS (EXCLUSIVE OF ELECTRICITY)
|  | GAS (Xcel) |  | 95874 | Therm x | 0.41931 |  | 40200.5434
|  | #6 Oil (Marathon) |  |  | Gallon x |  |  | 0
|  | #2 Fuel Oil |  |  | Gallon x |  |  | 0
|  | Water |  | 39.93 | 100cuft x | 3.86 |  | 154.1298
|  | Chem 939 |  | 6 | Gallon x | 13.52 |  | 81.12
|  |  | 960 | 4 | Pound x | 1.36 |  | 5.44
|  |  | 8540 | 4 | Gallon x | 14.49 |  | 57.96
|  |  | 9010 | 1.5 | Gallon x | 14.1 |  | 21.15
|  |  |  | TOTAL COST: |  |  |  | 40520.3432
| COST PER 1,000 LBS OF STEAM: | [6 empty] | 4.7778
ELECTRICITY USED:
|  | Xcel reading |  | 998400 | Kwh x | 0.042418 | = | 42350.1312
|  | HP reading |  | 1116863 | Kwh x | 0.042418 | = | 47375.0947
MONTHLY TEMPERATURES:
|  |  | Period High |  | 74 | ˚ F
|  |  | Period Low |  | 23 | ˚ F
|  |  | Ave. High |  | 47.9 | ˚ F
|  |  | Ave. Low |  | 35.3 | ˚ F
|  |  | Period Mean Temperature |  | 41.6 | ˚ F
DEGREE DAYS:
| Heating Degree Days |  |  | 725 |  | Cooling Degree Days |  |  | 0
CHILLER RUN TIME:
| New # 1 |  | 26 | Hours
| Old # 2 |  | 0 | Hours
| Chapel |  | 0 | Hours

## MgmtRpt
[5 empty] | MONTHLY MANAGEMENT REPORT | [5 empty] | MONTH: |  |  | YEAR:
DATE | CHILLER |  | HOUR |  | BOILER |  | STEAM FLOW X 1000 | GAS MCE | OIL | GAL | WATER GAL | ELECTRIC KWH |  | TEMP |  | DEG DAY
| 1 | 2 | 3 | 1 | 2 | 3 |  |  | #6 | #2 |  |  | HI | LO | AVG
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
AVG
TOTAL