## OpRpt
Main Meters
|  |  | Month: | November | Year: | 2003
Total Steam Flow (Lbs) From Meter |  |  |  | 10245000 | x 884 Btus |  |  | 9056580000 | Btus
FUEL:
|  | GAS (Xcel) |  | 120929 | Therms x 100,000 |  |  | 12092900000 | Btus | 130 Macalester
|  | #6 Oil (Marathon) |  | 0 | Gallons x 150,000 |  |  | 0 | Btus
|  | #2 Oil |  | 0 | Gallons x 138,000 |  |  | 0 | Btus
|  |  | TOTAL MONTHLY FUEL CONSUMPTION = |  |  |  |  | 12092900000 | Btus
|  | GAS | HP Meter | 11806 | MCF x 1,000,000 |  |  | 11806000000 | Btus | 130 Macalester
|  | #6 Oil HP Reading |  | 0 | Gallons x 150,000 |  |  | 0 | Btus
BOILER EFFICIENCY:
|  | Btu In Steam / Btu In Fuel = | [5 empty] | 74.89%
MAKE-UP WATER:
|  |  | 46360 | Gallons x 8.33 |  |  |  | 386178.8 | lbs
|  |  |  | [(Gallons/7.48cuft)/100] |  |  |  | 61.9786 | 100 cu.ft.
|  | LBS Make-Up Water / LBS Steam = | [5 empty] | 3.769% | Make-Up Water
BOILER OPERATIONAL COSTS (EXCLUSIVE OF ELECTRICITY)
|  | GAS (Xcel) |  | 71085 | Therm x | 0.58116 |  | 41311.4743
|  | #6 Oil (Marathon) |  |  | Gallon x |  |  | 0
|  | #2 Fuel Oil |  |  | Gallon x |  |  | 0
|  | Water |  | 61.9786 | 100cuft x | 3.89 |  | 241.0968
|  | Chem 938 |  | 2 | Gallon x | 13.52 |  | 27.04
|  |  | 960 | 5 | Pound x | 1.36 |  | 6.8
|  |  | 8588 | 5.5 | Gallon x | 14.49 |  | 79.695
|  |  | 9010 |  | Gallon x | 14.1 |  | 0
|  |  |  | TOTAL COST: |  |  |  | 41666.1061
| COST PER 1,000 LBS OF STEAM: | [6 empty] | 4.067
ELECTRICITY USED:
|  | Xcel reading |  | 1015200 | Kwh x | 0.034973 | = | 35504.5896 |  | 121 S Snelling
|  | HP reading |  | 1076231 | Kwh x | 0.034973 | = | 37639.0268
MONTHLY TEMPERATURES:
|  |  | Period High |  | 67 | ˚ F
|  |  | Period Low |  | 11 | ˚ F
|  |  | Ave. High |  | 40.2 | ˚ F
|  |  | Ave. Low |  | 26.1 | ˚ F
|  |  | Period Mean Temperature |  | 32.6 | ˚ F
DEGREE DAYS:
| Heating Degree Days |  |  | 969 |  | Cooling Degree Days |  |  | 0
CHILLER RUN TIME:
| New # 1 |  | n/a | Hours
| Old # 2 |  | n/a | Hours
| Chapel |  | n/a | Hours

## MgmtRpt
[5 empty] | MONTHLY MANAGEMENT REPORT | [5 empty] | MONTH: |  |  | YEAR:
DATE | CHILLER |  | HOUR |  | BOILER |  | STEAM FLOW X 1000 | GAS MCE | OIL | GAL | WATER GAL | ELECTRIC KWH |  | TEMP |  | DEG DAY
| 1 | 2 | 3 | 1 | 2 | 3 |  |  | #6 | #2 |  |  | HI | LO | AVG
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
AVG
TOTAL