## OpRpt
Main Meters
|  |  | Month: | May | Year: | 2004
Total Steam Flow (Lbs) From Meter |  |  |  | 2655000 | x 884 Btus |  |  | 2347020000 | Btus
FUEL:
|  | GAS (Xcel) |  | 23638 | Therms x 100,000 |  |  | 2363800000 | Btus | 130 Macalester
|  | #6 Oil (Marathon) |  | 0 | Gallons x 150,000 |  |  | 0 | Btus
|  | #2 Oil (Kath) |  | 0 | Gallons x 138,000 |  |  | 0 | Btus
|  |  | TOTAL MONTHLY FUEL CONSUMPTION = |  |  |  |  | 2363800000 | Btus
|  | GAS | HP Meter | 2360 | MCF x 1,000,000 |  |  | 2360000000 | Btus | 130 Macalester
|  | #6 Oil HP Reading |  | 0 | Gallons x 150,000 |  |  | 0 | Btus
|  | #2 Oil HP Reading |  | 0 | Gallons x 138,000 |  |  | 0 | Btus
BOILER EFFICIENCY:
|  | Btu In Steam / Btu In Fuel = | [5 empty] | 99.29%
MAKE-UP WATER:
|  |  | 12700 | Gallons x 8.33 |  |  |  | 105791 | lbs
|  |  |  | [(Gallons/7.48cuft)/100] |  |  |  | 16.9786 | 100 cu.ft.
|  | LBS Make-Up Water / LBS Steam = | [5 empty] | 3.985% | Make-Up Water
BOILER OPERATIONAL COSTS (EXCLUSIVE OF ELECTRICITY)
|  | GAS (Xcel) |  | 23638 | Therm x | 0.54095 |  | 12786.9761
|  | #6 Oil (Marathon) |  | 0 | Gallon x | 0.62 |  | 0
|  | #2 Fuel Oil (Kath) |  | 0 | Gallon x | 0.9005 |  | 0
|  | Water |  | 16.97 | 100cuft x | 4.15 |  | 70.4255 |  | 130 Macalester
|  | Chem 938 |  | 0 | Gallon x | 13.52 |  | 0
|  |  | 960 | 1 | Pound x | 1.36 |  | 1.36
|  |  | 8588 | 2 | Gallon x | 14.49 |  | 28.98
|  |  | 9010 |  | Gallon x | 14.1 |  | 0
|  |  |  | TOTAL COST: |  |  |  | 12887.7416
| COST PER 1,000 LBS OF STEAM: | [6 empty] | 4.8541
ELECTRICITY USED:
|  | Xcel reading |  | 888000 | Kwh x | 0.038207 | = | 33927.816 |  | 121 S Snelling
|  | HP reading |  | 933748 | Kwh x | 0.038207 | = | 35675.7098
MONTHLY TEMPERATURES:
|  |  | Period High |  | 82 | ˚ F
|  |  | Period Low |  | 37 | ˚ F
|  |  | Ave. High |  | 65.5 | ˚ F
|  |  | Ave. Low |  | 47.4 | ˚ F
|  |  | Period Mean Temperature |  | 56.2 | ˚ F
DEGREE DAYS:
| Heating Degree Days |  |  | 274 |  | Cooling Degree Days |  |  | 0
CHILLER RUN TIME:
| New # 1 |  | 101 | Hours
| Old # 2 |  | 11 | Hours
| Chapel |  | 0 | Hours

## MgmtRpt
[5 empty] | MONTHLY MANAGEMENT REPORT | [5 empty] | MONTH: |  |  | YEAR:
DATE | CHILLER |  | HOUR |  | BOILER |  | STEAM FLOW X 1000 | GAS MCE | OIL | GAL | WATER GAL | ELECTRIC KWH |  | TEMP |  | DEG DAY
| 1 | 2 | 3 | 1 | 2 | 3 |  |  | #6 | #2 |  |  | HI | LO | AVG
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
AVG
TOTAL