## OpRpt
Main Meters
|  |  | Month: | October | Year: | 2004
Total Steam Flow (Lbs) From Meter |  |  |  | 6382000 | x 884 Btus |  |  | 5641688000 | Btus
FUEL:
|  | GAS (Xcel) |  | 63558 | Therms x 100,000 |  |  | 6355800000 | Btus | 130 Macalester
|  | #6 Oil (Marathon) |  | 0 | Gallons x 150,000 |  |  | 0 | Btus
|  | #2 Oil |  | 0 | Gallons x 138,000 |  |  | 0 | Btus
|  |  | TOTAL MONTHLY FUEL CONSUMPTION = |  |  |  |  | 6355800000 | Btus
|  | GAS | HP Meter | 6278 | MCF x 1,000,000 |  |  | 6278000000 | Btus | 130 Macalester
|  | #6 Oil HP Reading |  | 0 | Gallons x 150,000 |  |  | 0 | Btus
BOILER EFFICIENCY:
|  | Btu In Steam / Btu In Fuel = | [5 empty] | 88.76%
MAKE-UP WATER:
|  |  | 22020 | Gallons x 8.33 |  |  |  | 183426.6 | lbs
|  |  |  | [(Gallons/7.48cuft)/100] |  |  |  | 29.4385 | 100 cu.ft.
|  | LBS Make-Up Water / LBS Steam = | [5 empty] | 2.874% | Make-Up Water
BOILER OPERATIONAL COSTS (EXCLUSIVE OF ELECTRICITY)
|  | GAS (Xcel) |  | 63558 | Therm x | 0.52294 |  | 33237.0205
|  | #6 Oil (Marathon) |  |  | Gallon x |  |  | 0
|  | #2 Fuel Oil |  |  | Gallon x |  |  | 0
|  | Water |  |  | 100cuft x | 3.89 |  | 0
|  | Chem 938 |  | 0 | Gallon x | 13.52 |  | 0
|  |  | 960 | 2 | Pound x | 1.36 |  | 2.72
|  |  | 8588 | 3.5 | Gallon x | 14.49 |  | 50.715
|  |  | 9010 |  | Gallon x | 14.1 |  | 0
|  |  |  | TOTAL COST: |  |  |  | 33290.4555
| COST PER 1,000 LBS OF STEAM: | [6 empty] | 5.2163
ELECTRICITY USED:
|  | Xcel reading |  | 1080000 | Kwh x | 0.038207 | = | 41263.56 |  | 121 S Snelling
|  | HP reading |  | 1100540 | Kwh x | 0.038207 | = | 42048.3318
MONTHLY TEMPERATURES:
|  |  | Period High |  | 74 | ˚ F
|  |  | Period Low |  | 29 | ˚ F
|  |  | Ave. High |  | 57.3 | ˚ F
|  |  | Ave. Low |  | 42.1 | ˚ F
|  |  | Period Mean Temperature |  | 49.4 | ˚ F
DEGREE DAYS:
| Heating Degree Days |  |  | 484 |  | Cooling Degree Days |  |  | 1
CHILLER RUN TIME:
| New # 1 |  | 58 | Hours
| Old # 2 |  | n/a | Hours
| Chapel |  | n/a | Hours

## MgmtRpt
[5 empty] | MONTHLY MANAGEMENT REPORT | [5 empty] | MONTH: |  |  | YEAR:
DATE | CHILLER |  | HOUR |  | BOILER |  | STEAM FLOW X 1000 | GAS MCE | OIL | GAL | WATER GAL | ELECTRIC KWH |  | TEMP |  | DEG DAY
| 1 | 2 | 3 | 1 | 2 | 3 |  |  | #6 | #2 |  |  | HI | LO | AVG
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
AVG
TOTAL