## Annual Summary 07-08
2007-2008 FUEL & ELECTRICTY CONSUMPTION (FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 0 | 0 | 0 | 3 | 5230 | 11601 | 15974 | 10573 | 12443 | 12744 | 7696 | 1791 | 78055
| COST-$ | 0 | 0 | 0 | 306.21 | 36287.47 | 92517.5 | 133628.87 | 87880.36 | 108252.1 | 122504.86 | 77871.16 | 21216.32 | 680464.85
| UNIT COST | 0 | 0 | 0 | 102.07 | 6.9383 | 7.975 | 8.3654 | 8.3118 | 8.6998 | 9.6127 | 10.1184 | 11.8461 | 8.7178
| MCF BTUS (x 1000) | 0 | 0 | 0 | 3000 | 5230000 | 11601000 | 15974000 | 10573000 | 12443000 | 12744000 | 7696000 | 1791000 | 78055000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6047 | 10909 | 0 | 0 | 0 | 16956
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17113.01 | 31745.19 | 0 | 0 | 0 | 48858.2
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.83 | 2.91 | 0 | 0 | 0 | 2.8815
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 834486 | 1505442 | 0 | 0 | 0 | 2339928
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 48356 | 10606 | 191 | 0 | 0 | 59202
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 58.8 | 44487.52 | 11878.72 | 246.39 | 0 | 0 | 56671.43
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0.92 | 1.12 | 1.29 | 0 | 0 | 0.95726
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 7350 | 7253400 | 1590900 | 28650 | 0 | 0 | 8880300
TOTAL HEATING BTU | QTY-BTU (x 1000) | 0 | 0 | 0 | 3000 | 5230000 | 11601000 | 15981350 | 18660886 | 15539342 | 12772650 | 7696000 | 1791000 | 89275228
TOTAL HEATING COSTS |  | 0 | 0 | 0 | 306.21 | 36287.47 | 92517.5 | 133687.67 | 149480.89 | 151876.01 | 122751.25 | 77871.16 | 21216.32 | 785994.48
ELECTRICITY | QUANTITY-KWH | 872200 | 982800 | 890400 | 1080800 | 905800 | 910000 | 996800 | 814800 | 950600 | 848400 | 889000 | 645657 | 10787257
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 32 | 28 | 32 | 29 | 32 | 33 | 30 | 29 | 30 | 30 | 37 | 372
| KWH PER DAY | 29073.3333 | 30712.5 | 31800 | 33775 | 31234.4828 | 28437.5 | 30206.0606 | 27160 | 32779.3103 | 28280 | 29633.3333 | 17450.1892 | 28998.0027
| COST-$ | 71047.17 | 88678.11 | 78241.95 | 72049.35 | 54836.99 | 59534.08 | 69111 | 60478.93 | 65735.48 | 60521.62 | 59102.9 | 56881.26 | 796218.84
| UNIT COST | 0.081457 | 0.09023 | 0.087873 | 0.066663 | 0.06054 | 0.065422 | 0.069333 | 0.074225 | 0.069152 | 0.071336 | 0.066482 | 0.088098 | 0.073811
Peak Demand (per Xcel billing) | QUANTITY KW | 1941 | 2308 | 2352 | 1776 | 1571 | 1939 | 1809 | 1633 | 1739 | 1851 | 1823 | 1764 | 1875.5
Peak Demand (per Xcel billing) | COST - $ | 16225.47 | 21349 | 21756 | 16428 | 10008.35 | 11459.49 | 10691.19 | 9651.03 | 10277.49 | 10939.41 | 10773.93 | 13250.58 | 162809.94
| BTUS (x 1000) | 2975946.4 | 3353313.6 | 3038044.8 | 3687689.6 | 3090589.6 | 3104920 | 3401081.6 | 2780097.6 | 3243447.2 | 2894740.8 | 3033268 | 2202981.684 | 36806120.884 | 0
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 2975.9464 | 3353.3136 | 3038.0448 | 3690.6896 | 8320.5896 | 14705.92 | 19382.4316 | 21440.9836 | 18782.7892 | 15667.3908 | 10729.268 | 3993.9817 | 126081.3489
# STEAM GENERATED |  | 0 | 0 | 0 | 0 | 4198000 | 9491000 | 15472000 | 16134000 | 15049000 | 12298000 | 7467000 | 3124000 | 83233000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 0% | 70.96% | 72.32% | 85.58% | 76.43% | 85.61% | 85.11% | 85.77% | 154.2% | 89.5%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 14 | 0 | 15 | 121 | 369 | 916 | 1472 | 1576 | 1413 | 1118 | 633 | 267 | 7914
COOLING DEGREE DAY - ACTUAL (MAC) |  | 214 | 316 | 209 | 107 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 880
Chiller Run Time - Central Plant (new chiller) |  | 390 | 463 | 423 | 276 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1684
Chiller Run Time - Central Plant (old chiller) |  | 254 | 338 | 332 | 211 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214
Chiller Run Time - Chapel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006-2007 FUEL & ELECTRICTY CONSUMPTION (FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 31 | 0 | 0 | 2489 | 7475 | 5288 | 145 | 746 | 247 | 5688 | 6122 | 773 | 29004
| COST-$ | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 42531.9 | 1508.66 | 5800.6 | 2263.36 | 46024.81 | 44747.94 | 6513.7 | 208186.32
| UNIT COST | 16.1142 | 0 | 0 | 7.3262 | 5.2764 | 8.0431 | 10.4046 | 7.7756 | 9.1634 | 0 | 7.3094 | 8.4265 | 7.1778
| MCF BTUS (x 1000) | 3100 | 0 | 0 | 2489000 | 7475000 | 5288000 | 145000 | 746000 | 247000 | 5688000 | 6122000 | 773000 | 29004000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 35200 | 70903 | 91598 | 98277 | 24630 | 0 | 0 | 320608
| COST-$ | 0 | 0 | 0 | 0 | 0 | 28864 | 67357.85 | 67782.52 | 75673.29 | 21920.7 | 0 | 0 | 261598.36
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0.82 | 0.95 | 0.74 | 0.77 | 0.89 | 0 | 0 | 0.81594
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 5280000 | 10635450 | 13739700 | 14741550 | 3694500 | 0 | 0 | 48091200
TOTAL HEATING BTU | QTY-BTU (x 1000) | 3100 | 0 | 0 | 2489000 | 7475000 | 10568000 | 10780450 | 14485700 | 14988550 | 9382500 | 6122000 | 773000 | 77067300
TOTAL HEATING COSTS |  | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 71395.9 | 68866.51 | 73583.12 | 77936.65 | 67945.51 | 44747.94 | 6513.7 | 469784.68
ELECTRICITY | QUANTITY-KWH | 1005600 | 1171200 | 1056000 | 1118400 | 1036800 | 1075200 | 1075200 | 938400 | 1048800 | 1070400 | 959000 | 844200 | 12399200
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 35 | 26 | 31 | 29 | 31 | 31 | 34 | 29 | 34 | 33 | 29 | 372
| KWH PER DAY | 33520 | 33462.8571 | 40615.3846 | 36077.4194 | 35751.7241 | 34683.871 | 34683.871 | 27600 | 36165.5172 | 31482.3529 | 29060.6061 | 29110.3448 | 33331.1828
| COST-$ | 63733.17 | 88526.74 | 82293.42 | 85211.58 | 72564.82 | 64331.44 | 64468.21 | 61057.55 | 65068.1 | 64259.32 | 67892.13 | 57182.14 | 836588.62
| UNIT COST | 0.063378 | 0.075586 | 0.077929 | 0.076191 | 0.069989 | 0.059832 | 0.059959 | 0.065066 | 0.062041 | 0.060033 | 0.070795 | 0.067735 | 0.067471
Peak Demand (per Xcel billing) | QUANTITY KW | 2280 | 3024 | 2568 | 2232 | 2520 | 2400 | 2016 | 1752 | 1920 | 1800 | 1752 | 1751 | 2167.9167
Peak Demand (per Xcel billing) | COST - $ | 17134 | 25129.44 | 21340.08 | 18547.92 | 16335.68 | 13584 | 11410.56 | 9916.32 | 11231.34 | 10638 | 10354.32 | 10348.41 | 175970.07
| BTUS (x 1000) | 3431107.2 | 3996134.4 | 3603072 | 3815980.8 | 3537561.6 | 3668582.4 | 3668582.4 | 3201820.8 | 3578505.6 | 3652204.8 | 3272108 | 2880410.4 | 42306070.4 | 0
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 3434.2072 | 3996.1344 | 3603.072 | 6304.9808 | 11012.5616 | 14236.5824 | 14449.0324 | 17687.5208 | 18567.0556 | 13034.7048 | 9394.108 | 3653.4104 | 119373.3704
# STEAM GENERATED |  | 0 | 0 | 0 | 1449000 | 6936000 | 8367000 | 11037000 | 11677000 | 11974000 | 7340000 | 6758000 | 1738000 | 67276000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 51.46% | 82.03% | 69.99% | 90.5% | 71.26% | 70.62% | 69.16% | 97.58% | 91% | 86.7%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 21 | 0 | 0 | 220 | 598 | 844 | 1115 | 1342 | 1432 | 837 | 549 | 124 | 7082
COOLING DEGREE DAY - ACTUAL (MAC) |  | 175 | 415 | 197 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 909
Chiller Run Time - Central Plant (new chiller) |  | 387 | 538 | 438 | 156 | 53 | 0 | 0 | 0 | 0 | 0 | 50 | 199 | 1821
Chiller Run Time - Central Plant (old chiller) |  | 287 | 385 | 344 | 119 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 1297
Chiller Run Time - Chapel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Summary page breaks
2007-2008 FUEL & ELECTRICTY CONSUMPTION
(FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 0 | 0 | 0 | 3 | 5230 | 11601 | 15974 | 10573 | 12443 | 12744 | 7696 | 1791 | 78055
| COST-$ | 0 | 0 | 0 | 306.21 | 36287.47 | 92517.5 | 133628.87 | 87880.36 | 108252.1 | 122504.86 | 77871.16 | 21216.32 | 680464.85
| UNIT COST | 0 | 0 | 0 | 102.07 | 6.9383 | 7.975 | 8.3654 | 8.3118 | 8.6998 | 9.6127 | 10.1184 | 11.8461 | 8.7178
| MCF BTUS (x 1000) | 0 | 0 | 0 | 3000 | 5230000 | 11601000 | 15974000 | 10573000 | 12443000 | 12744000 | 7696000 | 1791000 | 78055000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6047 | 10909 | 0 | 0 | 0 | 16956
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17113.01 | 31745.19 | 0 | 0 | 0 | 48858.2
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.83 | 2.91 | 0 | 0 | 0 | 2.8815
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 834486 | 1505442 | 0 | 0 | 0 | 2339928
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 48356 | 10606 | 191 | 0 | 0 | 59202
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 58.8 | 44487.52 | 11878.72 | 246.39 | 0 | 0 | 56671.43
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0.92 | 1.12 | 1.29 | 0 | 0 | 0.95726
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 7350 | 7253400 | 1590900 | 28650 | 0 | 0 | 8880300
TOTAL HEATING BTU | QTY-BTU (x 1000) | 0 | 0 | 0 | 3000 | 5230000 | 11601000 | 15981350 | 18660886 | 15539342 | 12772650 | 7696000 | 1791000 | 89275228
TOTAL HEATING COSTS |  | 0 | 0 | 0 | 306.21 | 36287.47 | 92517.5 | 133687.67 | 149480.89 | 151876.01 | 122751.25 | 77871.16 | 21216.32 | 785994.48
ELECTRICITY | QUANTITY-KWH | 872200 | 982800 | 890400 | 1080800 | 905800 | 910000 | 996800 | 814800 | 950600 | 848400 | 889000 | 645657 | 10787257
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 32 | 28 | 32 | 29 | 32 | 33 | 30 | 29 | 30 | 30 | 37 | 372
| KWH PER DAY | 29073.3333 | 30712.5 | 31800 | 33775 | 31234.4828 | 28437.5 | 30206.0606 | 27160 | 32779.3103 | 28280 | 29633.3333 | 17450.1892 | 28998.0027
| COST-$ | 71047.17 | 88678.11 | 78241.95 | 72049.35 | 54836.99 | 59534.08 | 69111 | 60478.93 | 65735.48 | 60521.62 | 59102.9 | 56881.26 | 796218.84
| UNIT COST | 0.081457 | 0.09023 | 0.087873 | 0.066663 | 0.06054 | 0.065422 | 0.069333 | 0.074225 | 0.069152 | 0.071336 | 0.066482 | 0.088098 | 0.073811
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 1941 | 2308 | 2352 | 1776 | 1571 | 1939 | 1809 | 1633 | 1739 | 1851 | 1823 | 1764 | 1875.5
Demand (per 121 S Snelling Xcel billing) | COST - $ | 16225.47 | 21349 | 21756 | 16428 | 10008.35 | 11459.49 | 10691.19 | 9651.03 | 10277.49 | 10939.41 | 10773.93 | 13250.58 | 162809.94
| BTUS (x 1000) | 2975946.4 | 3353313.6 | 3038044.8 | 3687689.6 | 3090589.6 | 3104920 | 3401081.6 | 2780097.6 | 3243447.2 | 2894740.8 | 3033268 | 2202981.684 | 36806120.884
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 2975.9464 | 3353.3136 | 3038.0448 | 3690.6896 | 8320.5896 | 14705.92 | 19382.4316 | 21440.9836 | 18782.7892 | 15667.3908 | 10729.268 | 3993.9817 | 126081.3489
# STEAM GENERATED |  | 0 | 0 | 0 | 0 | 4198000 | 9491000 | 15472000 | 16134000 | 15049000 | 12298000 | 7467000 | 3124000 | 83233000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 0% | 70.96% | 72.32% | 85.58% | 76.43% | 85.61% | 85.11% | 85.77% | 154.2% | 89.5%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 14 | 0 | 15 | 121 | 369 | 916 | 1472 | 1576 | 1413 | 1118 | 633 | 267 | 7914
COOLING DEGREE DAY - ACTUAL (MAC) |  | 214 | 316 | 209 | 107 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 880
Chiller Run Time - Central Plant (new chiller) |  | 390 | 463 | 423 | 276 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 1684
Chiller Run Time - Central Plant (old chiller) |  | 254 | 338 | 332 | 211 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1214
Chiller Run Time - Chapel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2006-2007 FUEL & ELECTRICTY CONSUMPTION
(FOR MAIN METERS ONLY)
|  | JUNE | JULY | AUGUST | SEP | OCT | NOV | DEC | JAN | FEB | MARCH | APRIL | MAY | YTD TOTAL
GAS | QUANTITY-MCF | 31 | 0 | 0 | 2489 | 7475 | 5288 | 145 | 746 | 247 | 5688 | 6122 | 773 | 29004
| COST-$ | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 42531.9 | 1508.66 | 5800.6 | 2263.36 | 46024.81 | 44747.94 | 6513.7 | 208186.32
| UNIT COST | 16.11 | 0 | 0 | 7.3262 | 5.2764 | 8.0431 | 10.4046 | 7.7756 | 9.1634 | 8.0916 | 7.3094 | 8.4265 | 7.1778
| MCF BTUS (x 1000) | 3100 | 0 | 0 | 2489000 | 7475000 | 5288000 | 145000 | 746000 | 247000 | 5688000 | 6122000 | 773000 | 29004000
#2 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| COST-$ | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#6 FUEL OIL | QUANTITY-GAL | 0 | 0 | 0 | 0 | 0 | 35200 | 70903 | 91598 | 98277 | 24630 | 0 | 0 | 320608
| COST-$ | 0 | 0 | 0 | 0 | 0 | 28864 | 67357.85 | 67782.52 | 75673.29 | 21920.7 | 0 | 0 | 261598.36
| UNIT COST | 0 | 0 | 0 | 0 | 0 | 0.82 | 0.95 | 0.74 | 0.77 | 0.89 | 0 | 0 | 0.81594
| BTUS (x 1000) | 0 | 0 | 0 | 0 | 0 | 5280000 | 10635450 | 13739700 | 14741550 | 3694500 | 0 | 0 | 48091200
TOTAL HEATING BTU | QTY-BTU (x 1000) | 3100 | 0 | 0 | 2489000 | 7475000 | 10568000 | 10780450 | 14485700 | 14988550 | 9382500 | 6122000 | 773000 | 77067300
TOTAL HEATING COSTS |  | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 71395.9 | 68866.51 | 73583.12 | 77936.65 | 67945.51 | 44747.94 | 6513.7 | 469784.68
ELECTRICITY | QUANTITY-KWH | 1005600 | 1171200 | 1056000 | 1118400 | 1036800 | 1075200 | 1075200 | 938400 | 1048800 | 1070400 | 959000 | 844200 | 12399200
(per 121 S Snelling Xcel billing) | # BILLING DAYS | 30 | 35 | 26 | 31 | 29 | 31 | 31 | 34 | 29 | 34 | 33 | 29 | 372
| KWH PER DAY | 33520 | 33462.8571 | 40615.3846 | 36077.4194 | 35751.7241 | 34683.871 | 34683.871 | 27600 | 36165.5172 | 31482.3529 | 29060.6061 | 29110.3448 | 33331.1828
| COST-$ | 63733.17 | 88526.74 | 82293.42 | 85211.58 | 72564.82 | 64331.44 | 64468.21 | 61057.55 | 65068.1 | 64259.32 | 67892.13 | 57182.14 | 836588.62
| UNIT COST | 0.063378 | 0.075586 | 0.077929 | 0.076191 | 0.069989 | 0.059832 | 0.059959 | 0.065066 | 0.062041 | 0.060033 | 0.070795 | 0.067735 | 0.067471
Demand (per 121 S Snelling Xcel billing) | QUANTITY KW | 2280 | 3024 | 2568 | 2232 | 2520 | 2400 | 2016 | 1752 | 1920 | 1800 | 1752 | 1751 | 2167.9167
Demand (per 121 S Snelling Xcel billing) | COST - $ | 17134 | 25129.44 | 21340.08 | 18547.92 | 16335.68 | 13584 | 11410.56 | 9916.32 | 11231.34 | 10638 | 10354.32 | 10348.41 | 175970.07
| BTUS (x 1000) | 3431107.2 | 3996134.4 | 3603072 | 3815980.8 | 3537561.6 | 3668582.4 | 3668582.4 | 3201820.8 | 3578505.6 | 3652204.8 | 3272108 | 2880410.4 | 42306070.4
TOTAL CAMPUS BTU CONSUMPTION x 1 MIL |  | 3434.2072 | 3996.1344 | 3603.072 | 6304.9808 | 11012.5616 | 14236.5824 | 14449.0324 | 17687.5208 | 18567.0556 | 13034.7048 | 9394.108 | 3653.4104 | 119373.3704
# STEAM GENERATED |  | 0 | 0 | 0 | 1449000 | 6936000 | 8367000 | 11037000 | 11677000 | 11974000 | 7340000 | 6758000 | 1738000 | 67276000
BOILER EFFICIENCY (BTU STEAM/BTU FUEL) |  | 0% | 0% | 0% | 51.46% | 82.03% | 69.99% | 90.5% | 71.26% | 70.62% | 69.16% | 97.58% | 91% | 86.7%
HEATING DEGREE DAY - ACTUAL (MAC) |  | 21 | 0 | 0 | 220 | 598 | 844 | 1115 | 1342 | 1432 | 837 | 549 | 124 | 7082
COOLING DEGREE DAY - ACTUAL (MAC) |  | 175 | 415 | 197 | 32 | 8 | 0 | 0 | 0 | 0 | 0 | 11 | 71 | 909
Chiller Run Time - Central Plant (new chiller) |  | 387 | 538 | 438 | 156 | 53 | 0 | 0 | 0 | 0 | 0 | 50 | 199 | 1821
Chiller Run Time - Central Plant (old chiller) |  | 287 | 385 | 344 | 119 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 1297
Chiller Run Time - Chapel |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## KWH Consumption
Electricity kwh
Year | June | July | August | September | October | November | December | January | February | March | April | May | Total
1991-92 (10,699,200 kwh) | 789600 | 1024800 | 878400 | 976800 | 873600 | 890400 | 931200 | 724800 | 1027200 | 818400 | 952800 | 811200 | 10699200
1992-93 (10,420,800 kwh) | 715200 | 861600 | 681600 | 876000 | 768000 | 988800 | 912000 | 914400 | 1089600 | 888000 | 957600 | 768000 | 10420800
1993-94 (10,384,173 kwh) | 722400 | 741600 | 782400 | 905013 | 935180 | 896884 | 915796 | 870500 | 1070400 | 825600 | 847200 | 871200 | 10384173
1994-95 (10,454,200 kwh) | 820800 | 763000 | 868800 | 957600 | 686400 | 955200 | 1018286 | 925714 | 981600 | 871200 | 955200 | 650400 | 10454200
1995-96 (10,836,825 kwh) | 840000 | 843200 | 768800 | 792525 | 924000 | 955460 | 987320 | 987320 | 972580 | 972500 | 947890 | 845230 | 10836825
1996-97 (11,988,879 kwh) | 727680 | 1204800 | 691200 | 1070400 | 960000 | 998400 | 1039898 | 1074562 | 1135139 | 1036800 | 972000 | 1078000 | 11988879
1997-98 (12,782,400 kwh) | 940800 | 979200 | 1008000 | 1135200 | 1144800 | 1096800 | 1195200 | 936000 | 1034400 | 1161600 | 1039200 | 1111200 | 12782400
1998-99 (12,979,200 kwh) | 1012800 | 1022400 | 1212000 | 1128000 | 1128000 | 945600 | 1195200 | 1056000 | 1101600 | 1039200 | 1130400 | 1008000 | 12979200
1999-00 (12,117,600 kwh) | 974400 | 1123200 | 1125600 | 1096800 | 1020000 | 1099200 | 849600 | 1020000 | 1039200 | 936000 | 878400 | 955200 | 12117600
2000-01 (11,611,968 kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
2001-02 (12,739,200 kwh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
2002-03 (13,257,600 kwh) | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
2003-04 (12,969,000 kwh) | 967200 | 1039200 | 1240800 | 1159200 | 1257600 | 1015200 | 1180800 | 1041600 | 1060800 | 844800 | 1274400 | 888000 | 12969600
2004-05 (12,969,000 kwh) | 899585 | 1105860 | 977142 | 1265510 | 1079949 | 1045310 | 1015844 | 1087376 | 1196023 | 1237149 | 1045415 | 989008 | 12944171
2005-06 (13,058,757 kwh) | 1029339 | 1209515 | 1077824 | 1224364 | 1065547 | 1007698 | 1236344 | 1033577 | 1140243 | 1071488 | 1012501 | 950317 | 13058757
2006-07 (11,177,000 kwh) | 1005600 | 1171200 | 1056000 | 1118400 | 1036800 | 1075200 | 1075200 | 938400 | 1048800 | 1070400 | 959000 | 844200 | 12399200
2007-08 (10,787,257 kwh) | 872200 | 982800 | 890400 | 1080800 | 905800 | 910000 | 996800 | 814800 | 950600 | 848400 | 889000 | 645657 | 10787257
TOTAL | 14462204 | 16775975 | 15781366 | 16764084 | 16019268 | 16253448 | 16360880 | 15694537 | 18044985 | 15536977 | 16365126 | 14535523 | 191643773
5 YEAR AVERAGE | 954784.8 | 1101715 | 1048433.2 | 1169654.8 | 1069139.2 | 1010681.6 | 1100997.6 | 983150.6 | 1079293.2 | 1014447.4 | 1036063.2 | 863436.4 | 12431797

## 3 yr KWH Chart
JUN JUL AUG SEP OCT NOV DEC JAN FEB MAR APR MAY
MAY
11,611,968Kwh
11,611,968Kwh
11611968
Kwh
12,117,900Kwh

## Electrical Cost
COST | B | C | D | E | F | G |  | H | I | J | K | L | M
ELECTRICITY TOTAL COST
YEAR | JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1989-90 | 40002.4 | 43554.85 | 39046.44 | 47470.22 | 36457.51 | 40253.02 | 39151.3 | 34274.9 | 32454.02 | 25671.79 | 38774.29 | 45942.72 | 463053.46
1991-92 | 41113.47 | 50860.74 | 47208.14 | 49653.69 | 37847.85 | 37085.37 | 36864.35 | 30817.13 | 39190.54 | 33672.49 | 37280.92 | 32377.89 | 473972.58
1992-93 | 38314.85 | 42152.25 | 37079.75 | 46777.86 | 33218.57 | 40339.61 | 37360.15 | 39558.76 | 46266.57 | 38935.94 | 43266.57 | 36921.27 | 480192.15
1993-94 | 40091.94 | 40591.98 | 44375.95 | 43186.49 | 44626.02 | 41549.88 | 40723.46 | 37921.42 | 44894.64 | 36792.89 | 37620.55 | 35346.3 | 487721.52
1994-95 | 45600.2 | 44893.52 | 52046.86 | 52102.41 | 31287.66 | 42689.29 | 43780.36 | 39800.33 | 40413.64 | 39014.34 | 41888.24 | 34366.22 | 507883.07
1995-96 | 46925.95 | 51452.69 | 46912.74 | 43310.12 | 41541.3 | 41915.28 | 43312.45 | 43312.45 | 41359.76 | 43473.7 | 43714.81 | 44719.41 | 531950.66
1996-97 ($559,179) | 36089.46 | 55056.45 | 46912.74 | 56136.57 | 44123.69 | 45668.97 | 44214.67 | 45688.5 | 47543.95 | 44095.82 | 46660.08 | 46988.51 | 559179.41
1997-98 ($613,894) | 51716.17 | 50880.21 | 52281.52 | 64303.48 | 56190.32 | 49899.49 | 50752.79 | 42517.47 | 46017.2 | 48439.02 | 48518 | 52378.32 | 613893.99
1998-99 ($626,968) | 56859.53 | 54769.44 | 61577.19 | 61033.56 | 52785.32 | 46722.9 | 51000.75 | 45236.65 | 49097.71 | 47346.81 | 53244.68 | 47022.4 | 626696.94
1999-00 ($621,699) | 51795.48 | 60748.07 | 59773.29 | 64595.98 | 52768.07 | 51195.01 | 51791.91 | 46138.66 | 47863.36 | 45512.26 | 47971.26 | 41545.57 | 621698.92
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($640,022) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
2002-03 ($637,914) | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
2003-04 ($639,256) | 55074.63 | 58882.69 | 68025.47 | 59587.77 | 60317.21 | 45625.39 | 52572.23 | 47503.98 | 49614.92 | 39192.97 | 56545.28 | 46313.9 | 639256.44
2004-05 ($677,250) | 54260.62 | 63469.84 | 56512.7 | 68456.06 | 53441.57 | 53882.23 | 50785.28 | 50212.8 | 58761.35 | 57560.21 | 55329.03 | 54578.99 | 677250.68
2005-06 ($807,129) | 68546.08 | 76184.17 | 79427.8 | 78117.58 | 61548.14 | 57570.61 | 68579.44 | 63251.23 | 75515.97 | 65617.58 | 60893.45 | 51877.3 | 807129.35
2006-07 ($770,180) | 63733.17 | 88526.74 | 82293.42 | 85211.58 | 72564.82 | 64331.44 | 64468.21 | 61057.55 | 65068.1 | 64259.32 | 67892.13 | 57182.14 | 836588.62
2007-08 ($000,000) | 71047.17 | 88678.11 | 78241.95 | 72049.35 | 54836.99 | 59534.08 | 69111 | 60478.93 | 65735.48 | 60521.62 | 59102.9 | 56881.26 | 796218.84
Previous five years (average) | 62532.334 | 75148.31 | 72900.268 | 72684.468 | 60541.746 | 56188.75 | 61103.232 | 56500.898 | 62939.164 | 57430.34 | 59952.558 | 53366.718 | 751288.786

## KW Demand
ELECTRICITY DEMAND KW | B | C | D | E | F | G | H | I | J | K | L | M | N
| JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1991-92 | 1940 | 1940 | 2040 | 2112 | 1800 | 1704 | 1704 | 1704 | 1656 | 1704 | 1704 | 2112 | 22120
1992-93 | 1968 | 1920 | 1968 | 2112 | 2040 | 1824 | 1800 | 1704 | 1776 | 1752 | 1776 | 1992 | 22632
1993-94 | 1968 | 1944 | 2112 | 1920 | 1920 | 1752 | 1752 | 1752 | 1872 | 1776 | 1776 | 1944 | 22488
1995-96 | 1992 | 2088 | 2088 | 1992 | 1608 | 1776 | 1776 | 1776 | 1776 | 1920 | 1920 | 1992 | 22704
1996-97 | 2064 | 2136 | 2184 | 2280 | 1968 | 2112 | 1968 | 1968 | 1896 | 1920 | 2256 | 1896 | 24648
1997-98 | 2232 | 2280 | 2040 | 2592 | 2592 | 2256 | 2040 | 1872 | 1992 | 2016 | 2208 | 2328 | 26448
1998-99 | 2376 | 2208 | 2280 | 2448 | 2208 | 2208 | 1920 | 1824 | 2040 | 2016 | 2256 | 2328 | 26112
1999-2000
2000-2001
2001-2002 | 2230 | 2230 | 2230 | 2230 | 2001 | 2136 | 2105 | 2093 | 2133 | 2081 | 2500 | 1970 | 25939
2002-2003 | 2711 | 2653 | 2330 | 2778 | 2477 | 2136 | 2208 | 2112 | 2196 | 2134 | 2712 | 2292 | 28739
2003-2004 | 2429 | 2526 | 2626 | 2759 | 2833 | 2208 | 2112 | 2136 | 2127 | 2098 | 2237 | 2189 | 28280
2004-2005 | 2228 | 2298 | 2077 | 2494 | 2624 | 2133 | 2092 | 1937 | 2349 | 2161 | 2500 | 2340 | 27233
2005-2006 | 2500 | 2500 | 2500 | 2393 | 2439 | 2163 | 2141 | 2009 | 2103 | 2088 | 2339 | 1992 | 27167
2006-2007 | 2280 | 3024 | 2568 | 2232 | 2520 | 2400 | 2016 | 1752 | 1920 | 1800 | 1752 | 1751 | 26015
2007-2008 | 1941 | 2308 | 2352 | 1776 | 1571 | 1939 | 1809 | 1633 | 1739 | 1851 | 1823 | 1764 | 22506
PREV. 3 YRS. AVG. | 2240.3333 | 2610.6667 | 2473.3333 | 2133.6667 | 2176.6667 | 2167.3333 | 1988.6667 | 1798 | 1920.6667 | 1913 | 1971.3333 | 1835.6667 | 25229.3333

## KW Demand Cost
ELECTRICITY DEMAND KW COST
| JUNE | JULY | AUGUST | SEPTEMBER | OCTOBER | NOVEMBER | DECEMBER | JANUARY | FEBRUARY | MARCH | APRIL | MAY | TOTAL
1992-93 | 15192.96 | 14822.4 | 15192.96 | 11302.08 | 10423.68 | 9959.04 | 9828 | 9303.84 | 9696.96 | 9565.92 | 9696.96 | 10876.32 | 135861.12
1993-94 | 15195.96 | 14822.4 | 16304.34 | 12968.46 | 12968.46 | 9565.92 | 9565.92 | 9565.92 | 10221.12 | 9696.96 | 10052.16 | 11003.04 | 141930.66
1994-95 | 16553.52 | 19086.41 | 17929.65 | 14404.55 | 10019.17 | 11003 | 11369.81 | 11369.81 | 12669.7 | 11229.44 | 11740.28 | 13838.76 | 161214.1
1995-96 | 16553 | 19086 | 17929 | 14404 | 10019 | 11003 | 11369 | 11369 | 12669 | 11229 | 11740 | 13868 | 161238
1996-97 | 13721 | 17158 | 18149 | 18947 | 11138 | 11954 | 11510 | 11510 | 11320 | 10867 | 12769 | 10731 | 159774
1997-98 | 18547 | 18947 | 16952 | 21539 | 14670 | 12769 | 11546 | 10595 | 11275 | 11411 | 12497 | 13176 | 173924
1998-99 | 19744.56 | 18348.48 | 18946.8 | 20342.88 | 12497.82 | 12497.28 | 10867.2 | 10323.84 | 11546 | 11411 | 12769 | 13176 | 172470.86
1999-2000
2000-2001 | 17550.72 | 18531.3 | 23593.75 | 14963.35 | 10595.52 | 10595.52 | 10052.15 | 10595.52 | 10609.1 | 7607.04 | 12361.44 | 8422.08 | 155477.49
2001-2002 | 19013.9 | 20473.14 | 19784.5 | 14532.82 | 13255.72 | 12089.76 | 11914.3 | 15400.28 | 9658.22 | 11778.46 | 14080.8 | 11150.2 | 173132.1
2002-2003 | 19993.39 | 21307.44 | 18878.6 | 21742.44 | 12443.62 | 12089.76 | 12497.28 | 11953.91 | 12429.36 | 14561.1 | 13454.6 | 12525.42 | 183876.92
2003-2004 | 18505.86 | 19436.31 | 21007.56 | 20888.84 | 14703.56 | 12497.28 | 11953.91 | 12089.76 | 12038.82 | 9142.26 | 14349.6 | 12389.74 | 179003.5
2004-2005 | 18514.68 | 19096.38 | 17259.87 | 17486.83 | 14150 | 12072.78 | 11840.72 | 10963.42 | 15124.45 | 13913.97 | 16096.69 | 15066.5 | 181586.29
2005-2006 | 19450 | 20775 | 20775 | 19885.83 | 15420.58 | 12242.58 | 12118.06 | 11370.94 | 11902.98 | 11818.08 | 13238.74 | 11274.72 | 180272.51
2006-2007 | 17134 | 25129.44 | 21340.08 | 18547.92 | 16335.68 | 13584 | 11410.56 | 9916.32 | 11231.34 | 10638 | 10354.32 | 10348.41 | 175970.07
2007-2008 | 16225.47 | 21349 | 21756 | 16428 | 10008.35 | 11459.49 | 10691.19 | 9651.03 | 10277.49 | 10939.41 | 10773.93 | 13250.58 | 162809.94
PREV. 3 YEARS AVERAGE | 17603.1567 | 22417.8133 | 21290.36 | 18287.25 | 13921.5367 | 12428.69 | 11406.6033 | 10312.7633 | 11137.27 | 11131.83 | 11455.6633 | 11624.57 | 173017.5067

## 3 yr Elec Cost-Consump
3 YEAR ELECTRICAL COST/CONSUMPTION COMPARISON

## ELECOMs
1996-97 ($559,179) | 36089.46 | 55056.45 | 46912.74 | 56136.57 | 44123.69 | 45668.97 | 44214.67 | 45688.5 | 47543.95 | 44095.82 | 46660.08 | 46988.51 | 559179.41
1997-98 ($613,894) | 51716.17 | 50880.21 | 52281.52 | 64303.48 | 56109.32 | 49899.49 | 50752.79 | 42517.47 | 46017.2 | 48439.02 | 48518 | 52378.32 | 613812.99
1998-99 ($626,696) | 56859.53 | 54769.44 | 61577.19 | 61033.56 | 52785.32 | 46722.9 | 51000.75 | 45236.65 | 49097.71 | 47346.81 | 53244.68 | 52378.32 | 632052.86
1999-00 ($621,699) | 51795.48 | 60748.07 | 59773.29 | 64595.98 | 52768.07 | 51195.01 | 51791.91 | 46138.66 | 47863.36 | 45512.26 | 47971.26 | 41545.57 | 621698.92
1996-97 (11,988,879 kwh) | 727680 | 1204800 | 691200 | 1070400 | 960000 | 998400 | 1039898 | 1074562 | 1135139 | 1036800 | 972000 | 1078000 | 11988879
1997-98 (12,782,400 kwh) | 940800 | 979200 | 1008000 | 1135200 | 1144800 | 1096800 | 1195200 | 936000 | 1034400 | 1161600 | 1039200 | 1111200 | 12782400
1998-99 (12,972,000 kwh) | 1012800 | 1022400 | 1212000 | 1128000 | 1128000 | 945600 | 1195200 | 1056000 | 1101600 | 1039200 | 1130400 | 1000800 | 12972000
1999-00 (12,117,600 kwh) | 974400 | 1123200 | 1125600 | 1096800 | 1020000 | 1099200 | 849600 | 1020000 | 1039200 | 936000 | 878400 | 955200 | 12117600
2000-01 (11,611,968 kwh) | 960000 | 1058400 | 1468800 | 891072 | 909792 | 876096 | 1096992 | 662688 | 1029600 | 692640 | 1048320 | 917568 | 11611968
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2000-01 ($567,550) | 50437.32 | 58385.34 | 75659.32 | 44676.62 | 40321.38 | 39542.88 | 48231.54 | 35124.09 | 50692.36 | 27815.23 | 48915.4 | 47748.59 | 567550.07
2001-02 ($642,002) | 60568.28 | 80559.47 | 58604.17 | 44218.28 | 60031.62 | 50221.63 | 41399.07 | 60250.73 | 40347.55 | 48772.09 | 53994.66 | 41054.88 | 640022.43
2002-03 ($637,914) | 59752.38 | 67141.22 | 57980.87 | 65093.01 | 42350.29 | 54781.48 | 40805.91 | 49771.51 | 51971.35 | 45086.04 | 51176.88 | 52002.85 | 637913.79
2003-04 ($639,256) | 55074.63 | 58882.69 | 68025.47 | 59587.77 | 60317.21 | 45625.39 | 52572.23 | 47503.98 | 49614.92 | 39192.97 | 56545.28 | 46313.9 | 639256.44
2004-05 ($677,251) | 54260.62 | 63469.84 | 56512.7 | 68456.06 | 53441.57 | 53882.23 | 50785.28 | 50212.8 | 58761.35 | 57560.21 | 55329.03 | 54578.99 | 677250.68
2005-06 ($807,129) | 68546.08 | 76184.17 | 79427.8 | 78117.58 | 61548.14 | 57570.61 | 68579.44 | 63251.23 | 75515.97 | 65617.58 | 60893.45 | 51877.3 | 807129.35
2006-07 ($836,589) | 63733.17 | 88526.74 | 82293.42 | 85211.58 | 72564.82 | 64331.44 | 64468.21 | 61057.55 | 65068.1 | 64259.32 | 67892.13 | 57182.14 | 836588.62
2007-08 ($796,219) | 71047.17 | 88678.11 | 78241.95 | 72049.35 | 54836.99 | 59534.08 | 69111 | 60478.93 | 65735.48 | 60521.62 | 59102.9 | 56881.26 | 796218.84
2001-02 (12,739,200Kwh) | 1000800 | 1365600 | 924000 | 837600 | 1231200 | 1116000 | 856800 | 1293600 | 926400 | 1094400 | 1243200 | 849600 | 12739200
2002-03 (13,257,600 kwh) | 1056000 | 1262400 | 1020000 | 1329600 | 998400 | 1291200 | 854400 | 1128000 | 1240800 | 976800 | 1101600 | 998400 | 13257600
2003-04 (12,969,600Kwh) | 967200 | 1039200 | 1240800 | 1159200 | 1257600 | 1015200 | 1180800 | 1041600 | 1060800 | 844800 | 1274400 | 888000 | 12969600
2004-05 (12,944,171Kwh) | 899585 | 1105860 | 977142 | 1265510 | 1079949 | 1045310 | 1015844 | 1087376 | 1196023 | 1237149 | 1045415 | 989008 | 12944171
2005-06 (13,058,757Kwh) | 1029339 | 1209515 | 1077824 | 1224364 | 1065547 | 1007698 | 1236344 | 1033577 | 1140243 | 1071488 | 1012501 | 950317 | 13058757
2006-07 (12,399,200Kwh) | 1005600 | 1171200 | 1056000 | 1118400 | 1036800 | 1075200 | 1075200 | 938400 | 1048800 | 1070400 | 959000 | 844200 | 12399200
2007-08 (10,787,257Kwh) | 872200 | 982800 | 890400 | 1080800 | 905800 | 910000 | 996800 | 814800 | 950600 | 848400 | 889000 | 645657 | 10787257

## Fuel Costs
COST OF GAS AND OIL
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1989-90 | 0 | 0 | 1671.63 | 7253.34 | 17630.36 | 32716.96 | 42366.81 | 44027.01 | 34538.38 | 27473.6 | 16807.89 | 5040.52 | 229526.5
1990-91 | 0 | 0 | 291.5 | 3837.1 | 16924.99 | 31880.28 | 46660.15 | 52425.97 | 38789.76 | 38003.13 | 15708.77 | 3301.84 | 247823.49
1991-92 | 290.13 | 290.13 | 290.13 | 2866.55 | 13910.59 | 24580.49 | 26474.94 | 29092.45 | 23169.06 | 19766.86 | 14441.43 | 4598 | 159770.76
1992-93 | 288.75 | 288.75 | 1392.574 | 8056.64 | 24858.19 | 33944.9 | 36597.08 | 37666.34 | 40480.24 | 39229.84 | 28818.27 | 7191.31 | 258812.884
1993-94 | 293.25 | 293.25 | 697.82 | 6527.91 | 19150.61 | 29301.55 | 31912.22 | 40397.79 | 35193.32 | 27280 | 16273.2 | 4786.13 | 212107.05
1994-95 | 288.75 | 288.75 | 1151.1 | 2292.35 | 10657.36 | 21758.26 | 30701.63 | 27292.94 | 19216.89 | 20358.27 | 16902.56 | 4753.26 | 155662.12
1995-96 | 288.75 | 288.75 | 288.75 | 4332.94 | 14332.72 | 26743.22 | 26190.43 | 32872.05 | 38188.42 | 34119.99 | 26100.05 | 8030.53 | 211776.6
1996-97 | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04 | 293146.26
1997-98 | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46 | 220834.4
1998-99 | 288.75 | 288.76 | 288.75 | 2018.24 | 18469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 199452.77
1999-00 ($221,413) | 288.75 | 288.755 | 288.75 | 983.5 | 20197.96 | 28859.89 | 35145.45 | 42257.41 | 36007.86 | 28525.76 | 24229.36 | 4339.67 | 221413.115
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($326,532) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54182.28 | 59123.34 | 51217.99 | 52101.56 | 35390.55 | 16235.31 | 326531.845
2002-03 ($432,450) | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
2003-04 ($423,755) | 309.25 | 314.99 | 309.25 | 9400.35 | 34165.61 | 62379.69 | 58806.6 | 78433.71 | 73578.58 | 54570.84 | 37895.53 | 13590.76 | 423755.16
2004-05 ($461,911) | 388.45 | 309.75 | 309.75 | 331.77 | 34964.75 | 47832.31 | 83109.12 | 95724.32 | 64052.589 | 76128.133 | 47603.27 | 11156.42 | 461910.632
2005-06 ($715,476) | 324.12 | 324.12 | 324.12 | 14185.86 | 110146.71 | 148118.98 | 129734.79 | 89203.79 | 96262.032 | 86711.97 | 30262.51 | 9876.74 | 715475.742
2006-07 ($421,140) | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 71395.9 | 66739.42 | 73583.12 | 77936.65 | 21428.1 | 44747.94 | 6513.7 | 421140.18
2007-08 ($785,944) | 0 | 0 | 0 | 306.21 | 36287.47 | 92517.5 | 133687.67 | 149480.89 | 151876.01 | 122751.25 | 77871.16 | 21216.32 | 785994.48
PREV. 5 YR. AVG. | 304.272 | 251.722 | 250.574 | 8491.812 | 51001.196 | 84448.876 | 94415.52 | 97285.166 | 92741.1722 | 72318.0586 | 47676.082 | 12470.788 | 561655.2388

## BTUCOMS
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
BTU CONSUMPTION (X100k) | [12 empty] | (x1,000,000)
1990-91 | 614 | 1002 | 0 | 1928 | 7874 | 11939 | 17525 | 19717 | 14558 | 14259 | 7891 | 1431 | 98738
1991-92 | 0 | 0 | 0 | 1202 | 7265 | 17945 | 14660 | 14841 | 13590 | 11751 | 8715 | 2299 | 92268
1992-93 | 0 | 0 | 409 | 2964 | 7393 | 12550 | 15372 | 16846 | 15458 | 9169 | 13671 | 2144 | 95976
1993-94 | 0 | 0 | 159 | 2305 | 7588 | 11335 | 12733 | 16627 | 14967 | 10545 | 6351 | 1961 | 84571
1994-95 | 0 | 0 | 275 | 1031 | 5650 | 9983 | 13049 | 14129 | 11594 | 10552 | 8831 | 2351 | 77445
1995-96 | 0 | 0 | 224 | 2249 | 7187 | 12545 | 13706 | 16049 | 14292 | 13114 | 9072 | 3371 | 91809
1996-97 | 0 | 0 | 0 | 0 | 8136 | 15131 | 17211 | 18573 | 14593 | 13176 | 7953 | 5218 | 99991
1997-98 | 0 | 0 | 0 | 0 | 6058 | 13793 | 14768 | 15811 | 11057 | 12651 | 6650 | 1626 | 82414
1998-99 | 0 | 0 | 0 | 901 | 7039 | 11084 | 15072 | 18574 | 12758 | 11701 | 7595 | 1964 | 86688
TOTAL | 68.2222 | 111.3333 | 118.5556 | 1397.7778 | 7132.2222 | 12922.7778 | 14899.5556 | 16796.3333 | 13651.8889 | 11879.7778 | 8525.4444 | 2485 | 89988.8889
COST OF GAS AND OIL
YEAR | JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY | TOTAL
1989-90 | 0 | 0 | 1671.63 | 7253.34 | 17630.36 | 32716.96 | 42366.81 | 44027.01 | 34538.38 | 27473.6 | 16807.89 | 5040.52 | 229526.5
1990-91 | 0 | 0 | 291.5 | 3837.1 | 16924.99 | 31880.28 | 46660.15 | 52425.97 | 38789.76 | 38003.13 | 15708.77 | 3301.84 | 247823.49
1991-92 | 290.13 | 290.13 | 290.13 | 2866.55 | 13910.59 | 24580.49 | 26474.94 | 29092.45 | 23169.06 | 19766.86 | 14441.43 | 4598 | 159770.76
1992-93 | 288.75 | 288.75 | 1392.574 | 8056.64 | 24858.19 | 33944.9 | 36597.08 | 37666.34 | 40480.24 | 39229.84 | 28818.27 | 7191.31 | 258812.884
1993-94 | 293.25 | 293.25 | 697.82 | 6527.91 | 19150.61 | 29301.55 | 31912.22 | 40397.79 | 35193.32 | 27280 | 16273.2 | 4786.13 | 212107.05
1994-95 | 288.75 | 288.75 | 1151.1 | 2292.35 | 10657.36 | 21758.26 | 30701.63 | 27292.94 | 19216.89 | 20358.27 | 16902.56 | 4753.26 | 155662.12
1995-96 | 288.75 | 288.75 | 288.75 | 4332.94 | 14332.72 | 26743.22 | 26190.43 | 32872.05 | 38188.42 | 34119.99 | 26100.05 | 8030.53 | 211776.6
1996-97 | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04 | 293146.26
1997-98 | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46 | 220834.4
1998-99 | 288.75 | 288.76 | 288.75 | 2018.24 | 18469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 199452.77
TOTAL | 174.426 | 174.426 | 868.7308 | 5708.308 | 18494.948 | 30484.836 | 36802.24 | 40721.912 | 34434.152 | 30350.686 | 18409.912 | 4983.56 | 127424.15
1996-97 (99.99 BIL Btus) | 0 | 0 | 0 | 0 | 8136 | 15131 | 17211 | 18573 | 14593 | 13176 | 7953 | 5218
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
1997-98 (82.41 BIL Btus) | 0 | 0 | 0 | 0 | 6058 | 13793 | 14768 | 15811 | 11057 | 12651 | 6650 | 1626
1998-99 (86.67 BIL Btus) | 0 | 0 | 0 | 901400 | 7039200 | 11084400 | 15061736 | 18574200 | 12758000 | 11700800 | 7595200 | 1964300 | 86679236
1999-00 (76.96 BIL Btus) | 0 | 0 | 0 | 220900 | 6917400 | 8867600 | 13369310 | 16118600 | 12526905 | 9955900 | 7720300 | 1262900 | 76959815
2000-01 (94.7 BIL Btus) | 0 | 0 | 0 | 468000 | 6354800 | 12605900 | 19682500 | 15766350 | 15803900 | 13307450 | 8176900 | 2535700 | 94701500
2001-02 (84.2 BIL Btus) | 0 | 0 | 0 | 1235500 | 7924900 | 8564900 | 13970210 | 14639200 | 11545805 | 13693100 | 8430600 | 4174700 | 84178915
1996-97 ($293,146) | 288.75 | 288.75 | 288.75 | 288.75 | 18560.04 | 45036.62 | 56549.53 | 76119.06 | 41494.11 | 25949.29 | 16174.57 | 12108.04
1997-98 ($220,834) | 288.75 | 288.75 | 288.75 | 288.75 | 20555.82 | 45722.06 | 38797.91 | 35106.45 | 26520.32 | 31884.38 | 16972 | 4120.46
1998-99 ($197,453) | 288.75 | 288.76 | 288.75 | 2018.24 | 16469.39 | 26298.58 | 37553.09 | 41044.13 | 27808.52 | 24531.35 | 15853.85 | 5009.36 | 197452.77
1999-00 ($221,394) | 288.75 | 288.755 | 288.75 | 983.5 | 20197.96 | 28859.89 | 35145.45 | 42257.41 | 35988.96 | 28525.76 | 24229.36 | 4339.67 | 221394.215
2000-01 ($506,962) | 288.75 | 288.75 | 308.75 | 2596.64 | 35860.04 | 59465.72 | 96326.24 | 93743.34 | 88344.05 | 70520.56 | 45814.83 | 13404.37 | 506962.04
2001-02 ($319,000) | 288.75 | 288.755 | 288.75 | 3851.42 | 18462.32 | 35100.82 | 54767.46 | 59123.34 | 45623.64 | 52101.56 | 33517.37 | 16235.31 | 319649.495
| JUN | JUL | AUG | SEP | OCT | NOV | DEC | JAN | FEB | MAR | APR | MAY
2002-03 (91.3 BIL Btus) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
2003-04 (89.5 BIL Btus) | 0 | 1000 | 0 | 1741000 | 7002000 | 11820000 | 15031250 | 16840950 | 16018546 | 11792050 | 6984000 | 2270000 | 89500796
2004-05 (BIL Btus) | 12000 | 0 | 0 | 4000 | 6286000 | 8603800 | 16086050 | 13577100 | 0 | 0 | 0 | 0 | 44568950
| 3081.384 | 3773.1943 | 3334.0085 | 4321.9201 | 9970.786 | 12170.3977 | 19552.1097 | 20947.2769 | 16151.1805 | 17148.6024 | 9928.956 | 4838.4953
2002-03 (91.3 BIL Btus) | 0 | 0 | 0 | 1319000 | 9450000 | 11736000 | 13188150 | 16308500 | 15462200 | 11278600 | 9711000 | 2881000 | 91334450
| 0 | 1000 | 0 | 1741000 | 7002000 | 11820000 | 15031250 | 16840950 | 16018546 | 11792050 | 6984000 | 2270000 | 89500796
2003-04 (133 BIL Btus) | 3300000 | 3547000 | 4234000 | 5696000 | 11293000 | 15284000 | 19060000 | 20395000 | 19638000 | 14675000 | 11332000 | 5300000 | 133753
2004-05 (125 BIL Btus) | 3081000 | 3773000 | 3334000 | 4322000 | 9971000 | 12170000 | 19552000 | 20947000 | 16151000 | 17149000 | 9929000 | 4838000 | 125218
2005-06 (122 BIL Btus) | 3512000 | 4127000 | 3678000 | 5545000 | 12987000 | 16508000 | 16723000 | 14399000 | 17281000 | 15613000 | 7863000 | 4604000 | 122839
2006-07 (115 BIL Btus) | 3434000 | 3996000 | 3603000 | 6305000 | 11013000 | 14237000 | 14449000 | 17688000 | 18567000 | 13035000 | 7273000 | 1604000 | 115203
2007-08 (126 BIL Btus) | 2976000 | 3353000 | 3038000 | 3691000 | 8321000 | 14706000 | 19382000 | 21441000 | 18783000 | 15667000 | 10729000 | 3994000 | 126081000
2002-03 ($432,450) | 309.25 | 309.25 | 309.25 | 4947.46 | 39439.27 | 56828.56 | 52623.49 | 67888.93 | 71725.89 | 70425.72 | 51597.23 | 16045.48 | 432449.78
2003-04 ($423,755) | 309.25 | 314.99 | 309.25 | 9400.35 | 34165.61 | 62379.69 | 58806.6 | 78433.71 | 73578.58 | 54570.84 | 37895.53 | 13590.76 | 423755.16
2004-05 ($461,911) | 388.45 | 309.75 | 309.75 | 331.77 | 34964.75 | 47832.31 | 83109.12 | 95724.32 | 64052.589 | 76128.133 | 47603.27 | 11156.42 | 461910.632
2005-06 ($715,476) | 324.12 | 324.12 | 324.12 | 14185.86 | 110146.71 | 148118.98 | 129734.79 | 89203.79 | 96262.032 | 86711.97 | 30262.51 | 9876.74 | 715475.742
2006-07 ($421,140) | 499.54 | 309.75 | 309.75 | 18234.87 | 39441.44 | 71395.9 | 66739.42 | 73583.12 | 77936.65 | 21428.1 | 44747.94 | 6513.7 | 421140.18
2007-08 ($785,994) | 0 | 0 | 0 | 306.21 | 36287.47 | 92517.5 | 133687.67 | 149480.89 | 151876.01 | 122751.25 | 77871.16 | 21216.32 | 785994.48

## BTU Chart
3 YEAR BTU/COST COMPARISON

## Heating Degree Days
| 90/91 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01 | 01/02 | 02/03 | 03/04 | 04/05 | 05/06 | 06/07 | 07/08 | 15 Year Avg. |  | 05/06 (6,545) | 06/07 (7082) | 07/08 (7914 ) | 3 Year Avg.
JUN | 25 | 48 | 38 | 29 | 6 | 30 | 30 | 10 | 80 | 68 | 64 | 63 | 35 | 47 | 72 | 1 | 21 | 14 | 38 | JUN | 1 | 21 | 14 | 12
JUL | 3 | 46 | 12 | 0 | 0 | 2 | 0 | 21 | 0 | 0 | 14 | 9 | 0 | 2 | 12 | 2 | 0 | 0 | 4.1333 | JUL | 2 | 0 | 0 | 0.66667
AUG | 1 | 79 | 21 | 2 | 0 | 0 | 0 | 29 | 1 | 5 | 1 | 5 | 4 | 0 | 58 | 5 | 0 | 15 | 8.3333 | AUG | 5 | 0 | 15 | 6.6667
SEP | 86 | 339 | 114 | 226 | 88 | 188 | 123 | 97 | 67 | 177 | 152 | 183 | 132 | 188 | 74 | 69 | 220 | 121 | 140.3333 | SEP | 69 | 220 | 121 | 136.6667
OCT | 425 | 668 | 493 | 462 | 336 | 485 | 438 | 465 | 465 | 489 | 364 | 513 | 725 | 448 | 484 | 431 | 598 | 369 | 471.4667 | OCT | 431 | 598 | 369 | 466
NOV | 689 | 1300 | 927 | 910 | 743 | 1038 | 1100 | 1068 | 826 | 682 | 1006 | 301 | 977 | 969 | 809 | 824 | 844 | 916 | 867.5333 | NOV | 824 | 844 | 916 | 861.3333
DEC | 1502 | 1441 | 1255 | 1155 | 1155 | 1346 | 1399 | 1160 | 1208 | 1189 | 1753 | 1148 | 1200 | 1227 | 1328 | 1390 | 1115 | 1472 | 1283 | DEC | 1390 | 1115 | 1472 | 1325.6667
JAN | 1722 | 1405 | 1384 | 1692 | 1275 | 1596 | 1502 | 1338 | 1558 | 1498 | 1350 | 1234 | 1540 | 1663 | 1537 | 1082 | 1342 | 1576 | 1452.2 | JAN | 1082 | 1342 | 1576 | 1333.3333
FEB | 1254 | 1151 | 1466 | 1277 | 1090 | 1275 | 1063 | 918 | 1033 | 1068 | 1440 | 1014 | 1372 | 1226 | 1073 | 1226 | 1432 | 1413 | 1194.6667 | FEB | 1226 | 1432 | 1413 | 1357
MAR | 1146 | 922 | 948 | 796 | 739 | 1155 | 945 | 1030 | 921 | 754 | 1113 | 1239 | 1043 | 908 | 1019 | 966 | 837 | 1118 | 972.2 | MAR | 966 | 837 | 1118 | 973.6667
APR | 639 | 406 | 513 | 513 | 581 | 608 | 481 | 395 | 480 | 559 | 504 | 615 | 529 | 481 | 396 | 335 | 549 | 633 | 510.6 | APR | 335 | 549 | 633 | 505.6667
MAY | 303 | 110 | 155 | 155 | 126 | 200 | 216 | 58 | 167 | 180 | 198 | 357 | 230 | 274 | 299 | 214 | 124 | 267 | 204.3333 | MAY | 214 | 124 | 267 | 201.6667
| 7795 | 7915 | 7326 | 7217 | 6139 | 7923 | 7297 | 6589 | 6806 | 6669 | 7959 | 6681 | 7787 | 7433 | 7161 | 6545 | 7082 | 7914 | 7146.8 |  | 6545 | 7082 | 7914 | 7180.3333

## Cooling Degree Days
MACALESTER COLLEGE ACTUAL READINGS
COOLING DEGREE DAYS
| 89/90 | 90/91 | 91/92 | 92/93 | 93/94 | 94-95 | 95-96 | 96-97 | 97-98 (690) | 98-99 (750) | 99-00 (740) | 00/01 (612) | 01/02 ( 851) | 02/03 (859) | 03/04 (772) | 04/05 (485) | 05/06 (932) | 06/07 (909) | 07/08 (880) | 3 YR AVE
JUN | 101 | 285 | 116 | 182 | 111 | 287 | 306 | 233 | 192 | 113 | 135 | 106 | 175 | 199 | 123 | 86 | 225 | 175 | 214 | 204.6667
JUL | 291 | 343 | 108 | 166 | 259 | 266 | 328 | 269 | 215 | 259 | 348 | 243 | 309 | 348 | 251 | 200 | 327 | 415 | 316 | 352.6667
AUG | 130 | 308 | 84 | 138 | 251 | 176 | 289 | 334 | 131 | 210 | 160 | 160 | 267 | 172 | 287 | 77 | 185 | 197 | 209 | 197
SEP | 12 | 166 | 7 | 32 | 9 | 101 | 72 | 104 | 34 | 125 | 54 | 49 | 44 | 115 | 92 | 110 | 89 | 32 | 107 | 76
OCT | 2 | 0 | 0 | 6 | 1 | 0 | 8 | 0 | 27 | 0 | 0 | 5 | 1 | 0 | 11 | 1 | 23 | 8 | 30 | 20.3333
NOV | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DEC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
JAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FEB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
APR | 3 | 0 | 16 | 0 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 8 | 20 | 11 | 8 | 5 | 1 | 11 | 0 | 4
MAY | 17 | 18 | 110 | 25 | 7 | 29 | 35 | 21 | 90 | 43 | 43 | 41 | 35 | 14 | 0 | 6 | 82 | 71 | 4 | 52.3333
TOTAL | 556 | 1121 | 441 | 549 | 645 | 859 | 1038 | 961 | 690 | 750 | 740 | 612 | 851 | 859 | 772 | 485 | 932 | 909 | 880 | 907

## Past Data
| ACTUAL | BTUs | TOTAL | FUEL |  | TOTAL | ELECT | TOTAL | TOTAL | TOTAL | BTU | COST
YEAR | HEATING | CONSUMED | FUEL | COST | KWH | ELECTRIC | COST | SQUARE | BTU | BTU | CONSUMP | per
| DEGREE | x1,000,000 | COST | per | CONSUMED | COST | per | FEET | CONSUM | COST | per FOOT | 1 MIL
| DAYS |  |  | 100k BTU |  |  | KWH |  | (x1 MIL) |  |  | BTUs
84-85 | 7632 | 100514 | 401058 | 0.39901 | 8767200 | 364038 | 0.041523 | 846365 | 130427.6864 | 765096 | 154103.3554 | 5.8661
85-86 | 7852 | 91852 | 328917 | 0.35809 | 8611200 | 361161 | 0.041941 | 846365 | 121233.4144 | 690078 | 143240.1085 | 5.6921
86-87 | 6238 | 86956 | 186058 | 0.21397 | 8407200 | 330664 | 0.039331 | 846365 | 115641.3664 | 516722 | 136632.9732 | 4.4683
87-88 | 7138 | 98071 | 235637 | 0.24027 | 8894600 | 376025 | 0.042276 | 846865 | 128419.3752 | 611662 | 151640.9052 | 4.763
88-89 (1) | 7817 | 100426 | 231792 | 0.23081 | 9900000 | 418470 | 0.04227 | 846365 | 134204.8 | 650262 | 158566.1033 | 4.8453
89-90 (2) | 8181 | 99062 | 232017 | 0.23421 | 9614400 | 431765 | 0.044908 | 938865 | 131866.3328 | 663782 | 140452.9222 | 5.0337
90-91 (3) | 7795 | 98739 | 251671 | 0.25489 | 10459200 | 463053 | 0.044272 | 944865 | 134425.7904 | 714724 | 142269.8379 | 5.3169
91-92 | 7915 | 92268 | 159770 | 0.17316 | 10699200 | 473973 | 0.0443 | 944865 | 128773.6704 | 633743 | 136287.904 | 4.9214
92-93 (4) | 7296 | 95977 | 165834.46 | 0.17279 | 10420800 | 480192 | 0.044 | 966865 | 131532.7696 | 646026.46 | 136040.4706 | 4.9115
93-94 (5) | 7098 | 85173 | 212107.05 | 0.24903 | 10384173 | 487721.55 | 0.046968 | 972865 | 120603.7983 | 699828.6 | 123967.6608 | 5.8027
94-95 | 6139 | 77444 | 155666.62 | 0.20101 | 10454200 | 509883.07 | 0.048773 | 972865 | 113113.7304 | 665550 | 116268.6811 | 5.8839
95-96 (6) | 7921 | 91589 | 211776 | 0.23122 | 10836825 | 531950.66 | 0.049087 | 972865 | 128564.2469 | 743726 | 132149 | 5.7849
96-97 (7) | 7297 | 99991 | 293146.26 | 0.29317 | 11983679 | 559179.31 | 0.046662 | 1018615 | 140879.3127 | 852325.57 | 139404 | 5.8647
97-98 (8) | 6589 | 82412 | 223641.54 | 0.27137 | 12782400 | 613894 | 0.048027 | 1056615 | 126025.5488 | 837535.54 | 119272.9128 | 6.6458
98-99 | 6788 | 86690 | 197452.77 | 0.22777 | 12972000 | 626697 | 0.048312 | 1056615 | 130950.464 | 824149.77 | 123933.9438 | 6.2936
99-00 (9) | 6669 | 76959 | 221394 | 0.28768 | 12117600 | 621699 | 0.051305 | 1053903 | 118370 | 843093 | 112315.8393 | 7.1225
00-01 (10) | 7959 | 94701 | 506962 | 0.53533 | 11611968 | 567550.07 | 0.048876 | 1149717 | 134321.0348 | 1074512.07 | 116829.6501 | 7.9996
01-02 (11) | 6681 | 85416 | 326532 | 0.38228 | 12739200 | 640022.43 | 0.05024 | 1187717 | 128882.1504 | 966554.43 | 108512.5079 | 7.4995
02-03 | 7787 | 91334 | 432449.78 | 0.47348 | 13257600 | 637913.79 | 0.048117 | 1187717 | 136568.9312 | 1070363.57 | 114984.4039 | 7.8375
03-04 (12) | 7433 | 89501 | 423755 | 0.47346 | 12969600 | 639256.44 | 0.049289 | 1187717 | 133753.2752 | 1063011.44 | 112613.7583 | 7.9476
04-05 (13) | 7161 | 107579.2115 | 461911 | 0.42937 | 12944171 | 677250.68 | 0.052 | 1208213 | 151744.7229 | 1139161.68 | 125594.3471 | 7.5071
05-06 | 6545 | 78282.15 | 715475.742 | 0.91397 | 13058757 | 807129.35 | 0.061808 | 1208213 | 122838.6289 | 1522605.092 | 101669.6798 | 12.3952
06-07 | 7082 | 77067 | 469784 | 0.60958 | 12399200 | 836588 | 0.067471 | 1208213 | 119373.0704 | 1306372 | 98801.3458 | 10.9436
07-08 | 7914 | 89275 | 785994 | 0.88042 | 10787257 | 796219 | 0.073811 | 1208213 | 126081.1209 | 1582213 | 104353.3888 | 12.5492
1. Library built and on line.
2. Weyerhaeuser Hall renovated--a/c added.
3. Carnegie Hall renovated--a/c added along with more usable area.
4. Humanities renovated--additional space and a/c.
5. Old Main renovated-additional space and a/c.
6. Rice renovation under way--construction heat throughout the year.
7. Rice operational with new mechanical systems, Olin's construction heat supplied by gas kiln meter--not reflected in this report.
8. New Residence Hall put on-line in August 1997. Additional 38,000 square feet of area. First air conditioned residence hall.
9. Old Dayton Hall and Student Union torn down summer of 1999. Temporary heat for Campus Center Construction.
10. Kagin taken out of operation during January 2001. Campus Center comes on line in January.
11. Kagin comes back on line January 2002.
12. Sold 1750 Summit and repurchased 1635 Summit as the new President's house. Completed renovation of Wallace Hall.
13. Completed renovation of Turck Hall.
14. Demolished Fieldhouse, pool, gym in fall 2006.
15. Winton Health Center demolished June '08 to make way for new Institute for Global Citizenship (IGC) building.
16. New Leonard Center opens August 08

## 0708 Budget
MACALESTER COLLEGE
MONTHLY ENERGY BUDGET REPORT
JUNE 2007 - MAY 2008
|  |  | BUDGETED | BUDGETED | 07 - 08 | 07 - 08
ENERGY | QUANTITY |  | CONSUMPTION | TOTAL | TOTAL | TOTAL
TYPE | CONSUMED | EXPENDITURE | (BTUs/KWH) | EXPENDITURE | CONSUMPTION | EXPENDITURE
GAS (MCF) | 78055 | 680465 |  |  | 78055 | 680465
OIL (GAL.)
#6 | 59202 | 56671 |  |  | 59202 | 56671
#2 | 16956 | 48858 |  |  | 16956 | 48858
TOTAL BTUs | 89275228 | 785994 | 88850000 | 888500 | 89275228 | 785994
(* 1,000)
ELEC. (KWH) | 10787257 | 796219 | 8500000 | 680000 | 10787257 | 796219
TOTAL
EXPENDED | 126081348.884 | 1582213 | 117852000 | 1568500 | 126081348.884 | 1582213
Variance:
|  |  |  | Budget -vs- Estimate |  | -13713
Fuel Variance:
|  |  |  | Consumption |  | 4252.28
|  |  |  | Price |  | -106758.28
|  |  |  | Sub-Total |  | -102506
Electrical Variance:
|  |  |  | Consumption |  | 182980.56
|  |  |  | Price |  | -66761.56
|  |  |  | Sub-Total |  | 116219
Total Variance
|  |  |  | Fuel & Electrical |  | 13713

## HDD vs Consump Stats
YEAR | HEATING | CONSUMED | FUEL | COST | KWH | ELECTRIC | COST | SQUARE | BTU | BTU | CONSUMP | per
| HDD | x1,000,000 | COST | PER | CONSUMED | COST | PER | FEET | CONSUM | COST | BTU | X1000K
90-91(3) | 7795 | 98739 | 251671 | 0.25489 | 10459200 | 463053 | 0.044272 | 944865 | 134425.7904 | 714724 | 142269.8379 | 5.3169
91-92 | 7915 | 92268 | 159770 | 0.17316 | 10699200 | 473973 | 0.0443 | 944865 | 128773.6704 | 633743 | 136287.904 | 4.9214
92-93(4) | 7296 | 95977 | 165834.46 | 0.17279 | 10420800 | 480192 | 0.044 | 966865 | 131532.7696 | 646026.46 | 136040.4706 | 4.9115
93-94(5) | 7098 | 85173 | 212107.05 | 0.24903 | 10384173 | 487721.55 | 0.046968 | 972865 | 120603.7983 | 699828.6 | 123967.6608 | 5.8027
94-95 | 6139 | 77444 | 155666.62 | 0.20101 | 10454200 | 509883.07 | 0.048773 | 972865 | 113140 | 665550 | 116295.6834 | 5.8825
95-96(6) | 7921 | 91589 | 211776 | 0.23122 | 10836825 | 531950.66 | 0.049 | 972865 | 128564 | 743726 | 132149 | 5.7849
96-97(7) | 7297 | 99991 | 293146.26 | 0.29317 | 11983679 | 559179.31 | 0.049 | 1018615 | 140880 | 852325.57 | 139404 | 5.8647
97-98(8) | 6589 | 82412 | 223641.54 | 0.27137 | 12782400 | 613894 | 0.048 | 1056615 | 120632 | 837535.54 | 114168.3584 | 6.9429
98-99 | 6806 | 86670 | 199452 | 0.23013 | 12972000 | 626697 | 0.048 | 1056615 | 131330 | 826149 | 124293.1437 | 6.2906
99-00(9) | 6698 | 77025 | 221699 | 0.28783 | 12117600 | 621699 | 0.051305 | 1053903 | 118370 | 843398 | 112315.8393 | 7.1251
00-01 (10) | 7959 | 94701 | 506962 | 0.53533 | 11611968 | 567550.07 | 0.048876 | 1149717 | 134321.0348 | 1074512.07 | 116829.6501 | 7.9996
01-02 (11) | 6681 | 85416 | 326532 | 0.38228 | 12739200 | 640022.43 | 0.05024 | 1187717 | 128882.1504 | 966554.43 | 108512.5079 | 7.4995
02-03 | 7787 | 91334 | 432449.78 | 0.47348 | 13257600 | 637913.79 | 0.048117 | 1187717 | 136568.9312 | 1070363.57 | 114984.4039 | 7.8375
03-04 | 7433 | 89501 | 423755.16 | 0.47346 | 12969600 | 639256.44 | 0.049289 | 1187717 | 133753.2752 | 1063011.6 | 112613.7583 | 7.9476
04-05 (13) | 7161 | 107579.2115 | 461911 | 0.42937 | 12944171 | 677250.68 | 0.052 | 1208213 | 151744.7229 | 1139161.68 | 125594.3471 | 7.5071
05-06 | 6545 | 78282.15 | 715475.742 | 0.91397 | 13058757 | 807129.35 | 0.061808 | 1208213 | 122838.6289 | 1522605.092 | 101669.6798 | 12.3952
06-07 | 7082 | 77067 | 469764 | 0.60955 | 11177000 | 770180 | 0.068908 | 1208213 | 115202.924 | 1239944 | 95349.8464 | 10.7631
07-08 | 7914 | 89275 | 785994 | 0.88042 | 10787257 | 796219 | 0.073811 | 1208213 | 126081.1209 | 1582213 | 104353.3888 | 12.5492
YEAR | HEATING | CONSUMED | FUEL COST | FUEL COST
| HDD | x10,000,000 | x10 | x100
90-91 | 7795 | 9873.9 | 25167.1 | 2516.71
91-92 | 7915 | 9226.8 | 15977 | 1597.7
92-93 | 7296 | 9597.7 | 16583.446 | 1658.3446
93-94 | 7098 | 8517.3 | 21210.705 | 2121.0705
94-95 | 6139 | 7744.4 | 15566.662 | 1556.6662
95-96 | 7921 | 9158.9 | 21177.6 | 2117.76
96-97 | 7297 | 9999.1 | 29314.626 | 2931.4626
97-98 | 6589 | 8241.2 | 22364.154 | 2236.4154
98-99 | 6788 | 8667 | 19945.2 | 1994.52
99-00 | 6669 | 7702.5 | 22169.9 | 2216.99
00-01 | 7959 | 9470.1 | 50696.2 | 5069.62
01-02 | 6681 | 8541.6 | 32653.2 | 3265.32
02-03 | 7787 | 9133.4 | 43244.978 | 4324.4978
03-04 | 7433 | 8950.1 | 42375.516 | 4237.5516
04-05 | 7161 | 10757.9211 | 46191.1 | 4619.11
05-06 | 6545 | 7828.215 | 71547.5742 | 7154.7574
06-07 | 7082 | 7828.215 | 71547.5742 | 7154.7574
07-08 | 7914 | 8927.5 | 78599.4 | 7859.94

## Condensate by Bldg
METER READINGS
|  | June |  | July |  | August |  | September |  | October |  | November |  | December |  | January |  | February |  | March |  | April |  | May | Annual
| 2007-06-03 |  | 2007-08-03 |  | 2007-09-04 |  | 2007-10-02 |  | 2007-11-01 |  | 2007-12-03 |  | 2008-01-02 |  | 2008-02-01 |  | 2008-03-03 |  | 2008-04-01 |  | 2008-05-01 |  | 2008-06-03 |  |  | %
| READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | READING | UNITS | TOTAL
ART & POWER PLANT | 5265370 | 0 | 5265370 | 0 | 5265370 | 0 | 5265710 | 340 | 5284850 | 19140 | 5352670 | 67820 | 5471130 | 118460 | 5545130 | 74000 | 5654010 | 108880 | 5707230 | 53220 | 5741090 | 33860 | 5753610 | 12520 | 435020 | 8.755%
CARNEGIE | 1532260 | 0 | 1532260 | 0 | 1532260 | 0 | 1532260 | 0 | 1536590 | 4330 | 1553180 | 16590 | 1579300 | 26120 | 1610990 | 31690 | 1639870 | 28880 | 1657980 | 18110 | 1667160 | 9180 | 1668970 | 1810 | 118600 | 2.387%
OLD MAIN | 1024530 | 0 | 1024530 | 0 | 1024530 | 0 | 1024530 | 0 | 1027860 | 3330 | 1046730 | 18870 | 1073080 | 26350 | 1105420 | 32340 | 1136700 | 31280 | 1155200 | 18500 | 1164890 | 9690 | 1167070 | 2180 | 124040 | 2.496%
LIBRARY | 1808080 | 0 | 1808080 | 0 | 1808080 | 0 | 1808080 | 0 | 1817510 | 9430 | 1841340 | 23830 | 1874180 | 32840 | 1911130 | 36950 | 1948050 | 36920 | 1979380 | 31330 | 1998280 | 18900 | 2004090 | 5810 | 164680 | 3.314%
WEYERHAEUSER HALL | 1144310 | 0 | 1144310 | 0 | 1144310 | 0 | 1144930 | 620 | 1153690 | 8760 | 1182240 | 28550 | 1222740 | 40500 | 1266080 | 43340 | 1307760 | 41680 | 1336670 | 28910 | 1357150 | 20480 | 1365630 | 8480 | 192410 | 3.872%
CHAPEL | 330770 | 0 | 330770 | 0 | 330770 | 0 | 331010 | 240 | 337530 | 6520 | 356220 | 18690 | 381980 | 25760 | 404390 | 22410 | 421970 | 17580 | 433060 | 11090 | 440500 | 7440 | 443200 | 2700 | 101340 | 2.04%
BIGELOW | 2315860 | 0 | 2315860 | 0 | 2315860 | 0 | 2315940 | 80 | 2328240 | 12300 | 2359800 | 31560 | 2405760 | 45960 | 2452160 | 46400 | 2497650 | 45490 | 2531360 | 33710 | 2555420 | 24060 | 2564720 | 9300 | 215150 | 4.33%
WALLACE & 30 MAC | 6736990 | 0 | 6736990 | 0 | 6736990 | 0 | 6736990 | 0 | 6752490 | 15500 | 6794470 | 41980 | 6845890 | 51420 | 6895580 | 49690 | 6951640 | 56060 | 6989110 | 37470 | 7013740 | 24630 | 7023390 | 9650 | 248930 | 5.01%
GD DAYTON | 1798800 | 0 | 1798800 | 0 | 1798800 | 0 | 1798800 | 0 | 1809100 | 10300 | 1836300 | 27200 | 1870300 | 34000 | 1905300 | 35000 | 1941800 | 36500 | 1966300 | 24500 | 1984100 | 17800 | 1990400 | 6300 | 167100 | 3.363%
DOTY | 164230 | 0 | 164230 | 0 | 164230 | 0 | 164230 | 0 | 190280 | 26050 | 246600 | 56320 | 326630 | 80030 | 394350 | 67720 | 471330 | 76980 | 537010 | 65680 | 588320 | 51310 | 607050 | 18730 | 377140 | 7.59%
TURCK | 1756920 | 0 | 1756920 | 0 | 1756920 | 0 | 1756920 | 0 | 1765800 | 8880 | 1793420 | 27620 | 1832940 | 39520 | 1869620 | 36680 | 1905670 | 36050 | 1932680 | 27010 | 1950590 | 17910 | 1955990 | 5400 | 172060 | 3.463%
DUPRE | 5236630 | 0 | 5236630 | 0 | 5236630 | 0 | 5236640 | 10 | 5259970 | 23330 | 5315390 | 55420 | 5396850 | 81460 | 5484490 | 87640 | 5567530 | 83040 | 5625080 | 57550 | 5662890 | 37810 | 5675330 | 12440 | 381150 | 7.671%
KAGIN | 1176530 | 0 | 1176530 | 0 | 1176530 | 0 | 1176530 | 0 | 1188200 | 11670 | 1221580 | 33380 | 1271280 | 49700 | 1324250 | 52970 | 1375770 | 51520 | 1411190 | 35420 | 1433950 | 22760 | 1441570 | 7620 | 229620 | 4.621%
CAMPUS CENTER | 781450 | 0 | 781450 | 0 | 781450 | 0 | 781450 | 0 | 841160 | 59710 | 918740 | 77580 | 976600 | 57860 | 1054880 | 78280 | 1111190 | 56310 | 1160330 | 49140 | 1226140 | 65810 | 1257800 | 31660 | 427210 | 8.598%
KIRK | 475490 | 0 | 475490 | 0 | 475490 | 0 | 475490 | 0 | 488460 | 12970 | 520600 | 32140 | 567380 | 46780 | 618660 | 51280 | 669860 | 51200 | 705910 | 36050 | 730660 | 24750 | 737470 | 6810 | 225930 | 4.547%
RICE | 17378100 | 0 | 17378100 | 0 | 17378100 | 0 | 17378100 | 0 | 17429500 | 51400 | 17485100 | 55600 | 17564300 | 79200 | 17604900 | 40600 | 17623100 | 18200 | 17693800 | 70700 | 17804900 | 111100 | 17842200 | 37300 | 393400 | 7.917%
MUSIC | 1424310 | 0 | 1424310 | 0 | 1424310 | 0 | 1424340 | 30 | 1440270 | 15930 | 1476840 | 36570 | 1527310 | 50470 | 1580870 | 53560 | 1633930 | 53060 | 1673470 | 39540 | 1702050 | 28580 | 1712150 | 10100 | 248300 | 4.997%
HUMANITIES | 5528110 | 0 | 5528110 | 0 | 5528110 | 0 | 5528110 | 0 | 5540240 | 12130 | 5578650 | 38410 | 5586140 | 7490 | 5639090 | 52950 | 5694070 | 54980 | 5727840 | 33770 | 5749640 | 21800 | 5763700 | 14060 | 201820 | 4.062%
DISTRICT HEATING | 2765960 | 0 | 2765960 | 0 | 2765960 | 0 | 2765960 | 0 | 2766000 | 40 | 2767110 | 1110 | 2769460 | 2350 | 2769840 | 380 | 2769840 | 0 | 2769890 | 50 | 2769890 | 0 | 2772910 | 3020 | 6900 | 0.1389%
THEATER | 367010 | 0 | 367010 | 0 | 367010 | 0 | 368970 | 1960 | 395820 | 26850 | 468480 | 72660 | 564690 | 96210 | 666610 | 101920 | 780470 | 113860 | 870880 | 90410 | 954390 | 83510 | 995470 | 41080 | 538050 | 10.83%
| 59011710 | 0 |  | 0 |  | 0 |  | 3280 |  | 338570 |  | 761900 |  | 992480 |  | 995800 |  | 998470 |  | 762160 |  | 631380 |  | 246970 | 4968850 | 100%

## Electrical Read by Bldg
LOCATION | May | JUNE |  | JULY |  | AUGUST |  | SEPTEMBER |  | OCTOBER |  | NOVEMBER |  | DECEMBER |  | JANUARY |  | FEBRUARY |  | MARCH |  | APRIL |  | MAY |  | ANNUAL | % OF
READ DATE | 2007-06-01 | 2007-07-01 |  | 2007-08-03 |  | 2007-09-04 |  | 2007-10-02 |  | 2007-11-01 |  | 2007-12-03 |  | 2008-01-02 |  | 2008-02-01 |  | 2008-03-03 |  | 2008-04-01 |  | 2008-05-01 |  | 2008-06-03
| Reading | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | Reading | Total | TOTAL | CAMPUS
MUSIC (PB1) | 1398 | 2019 | 12420 | 2764 | 14900 | 3629 | 17300 | 4311 | 13640 | 5286 | 19500 | 6209 | 18460 | 7518 | 26180 | 8999 | 29620 | 10699 | 34000 | 12041 | 26840 | 13263 | 24440 | 14393 | 22600 | 259900 | 1.967%
ART LIGHTS (TC) | 59418 | 59992 | 11480 | 60687 | 13900 | 61382 | 13900 | 62192 | 16200 | 63380 | 23760 | 64747 | 27340 | 65988 | 24820 | 67046 | 21160 | 68413 | 27340 | 69622 | 24180 | 70973 | 27020 | 71965 | 19840 | 250940 | 1.9%
THEATER (TA) | 27220 | 27786 | 11320 | 28361 | 11500 | 29058 | 13940 | 29994 | 18720 | 31208 | 24280 | 32630 | 28440 | 33808 | 23560 | 35073 | 25300 | 36692 | 32380 | 38018 | 26520 | 39404 | 27720 | 40389 | 19700 | 263380 | 1.994%
MUSIC LIGHTS (TB) | 41855 | 42175 | 6400 | 42539 | 7280 | 42927 | 7760 | 43297 | 7400 | 43756 | 9180 | 44260 | 10080 | 44729 | 9380 | 45234 | 10100 | 45793 | 11180 | 46253 | 9200 | 46792 | 10780 | 47229 | 8740 | 107480 | 0.8136%
CARNEGIE | 11545 | 11995 | 13500 | 12541 | 16380 | 13039 | 14940 | 13664 | 18750 | 14414 | 22500 | 15202 | 23640 | 15968 | 22980 | 16746 | 23340 | 17679 | 27990 | 18426 | 22410 | 19194 | 23040 | 19770 | 17280 | 246750 | 1.868%
POWER PLANT | 40230 | 40845 | 18450 | 41686 | 25230 | 42498 | 24360 | 42992 | 14820 | 43575 | 17490 | 44090 | 15450 | 44285 | 5850 | 44715 | 12900 | 45155 | 13200 | 45559 | 12120 | 46236 | 20310 | 46780 | 16320 | 196500 | 1.487%
CHILLER | 1024.98 | 1236.88 | 8476 | 1532.21 | 11813.2 | 1799.94 | 10709.2 | 1942.08 | 5685.6 | 1984.8 | 1708.8 | 1984.8 | 0 | 1984.8 | 0 | 1984.8 | 0 | 1984.8 | 0 | 1984.8 | 0 | 1984.8 | 0 | 2036.12 | 2052.8 | 40445.6 | 0.3062%
LIBRARY | 170 | 355 | 59200 | 575 | 70400 | 797 | 71040 | 1192 | 126400 | 1414 | 71040 | 1750 | 107520 | 2058 | 98560 | 2336 | 88960 | 2712 | 120320 | 3003 | 93120 | 3311 | 98560 | 3569 | 82560 | 1087680 | 8.233%
OLD MAIN | 8448 | 9112 | 13280 | 9904 | 15840 | 10675 | 15420 | 11469 | 15880 | 12375 | 18120 | 13442 | 21340 | 14757 | 26300 | 16186 | 28580 | 17681 | 29900 | 18797 | 22320 | 19734 | 18740 | 20507 | 15460 | 241180 | 1.826%
CHAPEL CHILLER | 47720 | 47746 | 1040 | 47775 | 1160 | 47804 | 1160 | 47830 | 1040 | 47831 | 40 | 47831 | 0 | 47831 | 0 | 47831 | 0 | 47831 | 0 | 47831 | 0 | 47831 | 0 | 47831 | 0 | 4440 | 0.03361%
CHAPEL | 21499 | 21923 | 12720 | 22389 | 13980 | 22868 | 14370 | 23241 | 11190 | 23635 | 11820 | 24056 | 12630 | 24449 | 11790 | 24852 | 12090 | 25256 | 12120 | 25609 | 10590 | 25965 | 10680 | 26229 | 7920 | 141900 | 1.074%
BIGELOW | 86098 | 86307 | 12540 | 86535 | 13680 | 86781 | 14760 | 87097 | 18960 | 87454 | 21420 | 87842 | 23280 | 88319 | 28620 | 88767 | 26880 | 89319 | 33120 | 89734 | 24900 | 90071 | 20220 | 90344 | 16380 | 254760 | 1.928%
WEY HALL | 39125 | 39552 | 8540 | 40047 | 9900 | 40554 | 10140 | 41043 | 9780 | 41585 | 10840 | 42108 | 10460 | 42700 | 11840 | 43341 | 12820 | 44006 | 13300 | 44580 | 11480 | 45108 | 10560 | 45593 | 9700 | 129360 | 0.9792%
WALLACE | 883934 | 894880 | 82095 | 906874 | 89955 | 919418 | 94080 | 936758 | 130050 | 955475 | 140377.5 | 975154 | 147592.5 | 990839 | 117637.5 | 1004190 | 100132.5 | 1004190 | 0 | 1004190 | 0 | 1051611 | 355657.5 | 1066220 | 109567.5 | 1367145 | 10.35%
DOTY | 32649 | 33218 | 17070 | 33982 | 22920 | 34605 | 18690 | 35373 | 23040 | 36166 | 23790 | 36983 | 24510 | 37644 | 19830 | 38211 | 17010 | 38958 | 22410 | 39635 | 20310 | 40340 | 21150 | 40945 | 18150 | 248880 | 1.884%
TURCK | 16529 | 16761 | 3480 | 17022 | 3915 | 17317 | 4425 | 17780 | 6945 | 18290 | 7650 | 18845 | 8325 | 19273 | 6420 | 19610 | 5055 | 20144 | 8010 | 20606 | 6930 | 21103 | 7455 | 21462 | 5385 | 69570 | 0.5266%
30 MAC | 42559 | 43366 | 6052.5 | 44303 | 7027.5 | 45283 | 7350 | 46560 | 9577.5 | 47946 | 10395 | 49414 | 11010 | 50600 | 8895 | 51600 | 7500 | 52945 | 10087.5 | 54166 | 9157.5 | 55476 | 9825 | 56640 | 8730 | 98257.5 | 0.7438%
GD DAYTON | 3951521 | 3975113 | 23592 | 4000837 | 25724 | 4026521 | 25684 | 4056087 | 29566 | 4088012 | 31925 | 4121761 | 33749 | 4167474 | 45713 | 4210697 | 43223 | 4258797 | 48100 | 4292089 | 33292 | 4316587 | 24498 | 4340150 | 23563 | 388629 | 2.942%
DUPRE | 1829967 | 1847889 | 117922 | 1864867 | 116978 | 1889656 | 124789 | 1932061 | 142405 | 1968866 | 136805 | 2003358 | 134492 | 2030458 | 127100 | 2051857 | 121399 | 2083699 | 131842 | 2110859 | 127160 | 2139871 | 129012 | 2161258 | 121387 | 1531291 | 11.59%
KAGIN | 1584461 | 1608135 | 123674 | 1633423 | 125288 | 1664640 | 131217 | 1692571 | 127931 | 1723034 | 130463 | 1751032 | 127998 | 1778186 | 127154 | 1803972 | 125786 | 1834926 | 130954 | 1860292 | 125366 | 1888568 | 128276 | 1914334 | 125766 | 1529873 | 11.58%
CAMPUS CENTER | 26297 | 79049 | 152752 | 98982 | 119933 | 99143 | 100161 | 8519.4 | 109376.4 | 30095.7 | 121576.3 | 61589.9 | 131494.2 | 71996.8 | 110406.9 | 83269.9 | 111273.1 | 20743.8 | 137473.9 | 32402 | 111658.2 | 51330 | 118928 | 49546.7 | 98216.7 | 1423249.7 | 10.77%
KIRK | 7079 | 7108 | 4640 | 7149 | 6560 | 7191 | 6720 | 7282 | 14560 | 7388 | 16960 | 7515 | 20320 | 7633 | 18880 | 7736 | 16480 | 7894 | 25280 | 8004 | 17600 | 8104 | 16000 | 8171 | 10720 | 174720 | 1.323%
LEONARD CENTER | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
MAIN VAULT | 1652 | 2257 | 18150 | 2988 | 21930 | 3707 | 21570 | 4375 | 20040 | 5028 | 19590 | 5691 | 19890 | 6318 | 18810 | 7066 | 22440 | 7642 | 17280 | 8240 | 17940 | 8855 | 18450 | 198 | 40290 | 256380 | 1.941%
STADIUM | 39043 | 39137 | 9400 | 39290 | 15300 | 39451 | 16100 | 39622 | 17100 | 39877 | 25500 | 40648 | 77100 | 41697 | 104900 | 42804 | 110700 | 43874 | 107000 | 44598 | 72400 | 45063 | 46500 | 45219 | 15600 | 617600 | 4.675%
RICE | 25203418 | 25358697 | 155279 | 25538004 | 179307 | 25701120 | 163116 | 25850325 | 149205 | 26009734 | 159409 | 26181860 | 172126 | 26324225 | 142365 | 26467051 | 142826 | 26625979 | 158928 | 26768681 | 142702 | 26929372 | 160691 | 27096632 | 167260 | 1893214 | 14.33%
HUM POW & LIG | 83261 | 84222 | 28830 | 85332 | 33300 | 86423 | 32730 | 87451 | 30840 | 88567 | 33480 | 89750 | 35490 | 90799 | 31470 | 91781 | 29460 | 92885 | 33120 | 93912 | 30810 | 95041 | 33870 | 96168 | 33810 | 387210 | 2.931%
SUBTOTAL |  |  | 932302.5 |  | 994100.7 |  | 976431.2 |  | 1089101.5 |  | 1109619.6 |  | 1242736.7 |  | 1169461.4 |  | 1145034.6 |  | 1185335.4 |  | 999005.7 |  | 1362382.5 |  | 1016998 | 13210734.8 | 1
MAIN METER |  |  | 872200 |  | 982800 |  | 890400 |  | 1080800 |  | 905800 |  | 910000 |  | 996800 |  | 814800 |  | 950600 |  | 848400 |  | 889000 |  | 645657 | 10787257
|  |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill) |  | (from Xcel Bill)
% OF MAIN METER |  |  | 106.9% |  | 101.1% |  | 109.7% |  | 100.8% |  | 122.5% |  | 136.6% |  | 117.3% |  | 140.5% |  | 124.7% |  | 117.8% |  | 153.2% |  | 157.5% | 122.5%

## Wind Turbine Data
| June | July | Aug. | Sept. | Oct. | Nov. | Dec. | Jan. | Feb. | March | April | May
Date
1 | 0.17 | 0 | 0 | 0 | 4.44 |  |  | 1.34 | 0.01 | 12.51 | 11.37 | 6.53
2 | 0.19 | 0.62 | 0 | 3.59 | 1.01 |  |  | 7.31 | 0.27 | 1.53 | 4.31 | 15.11
3 | 0.73 | 3.17 | 0 | 0.94 | 7.71 |  |  | 0.21 | 0 | 3.86 | 2.81 | 13.28
4 | 0.41 | 0.09 | 0 | 1.06 | 3.39 |  |  | 12.71 | 0.19 | 0.58 | 0 | 23.27
5 | 4.98 | 0.25 | 0 | 1.16 | 1.74 |  |  | 5.31 | 1.09 | 0.35 | 3.46 | 5.06
6 | 0.19 | 1.16 | 0 | 4.23 | 0.66 |  |  | 5.18 | 0.46 | 1.35 | 3.75 | 0.12
7 | 15.18 | 0 | 0 | 6.34 | 6.53 |  |  | 0.41 | 0.13 | 0 | 5.73 | 1.27
8 | 23.93 | 1.87 | 0.49 | 4.34 | 1.35 |  |  | 0.02 | 0 | 1.01 | 2.53 | 9.09
9 | 0 | 1.47 | 0.09 | 1.55 | 3.59 |  |  | 0.87 | 0.02 | 2.44 | 0.03 | 0
10 | 0 | 0 | 2.49 | 2.71 | 18.77 |  |  | 2.13 | 23.53 | 0.98 | 0.24 | 0.14
11 | 2.07 | 0 | 0.64 | 0.12 | 7.32 |  |  | 0.18 | 19.06 | 3.26 | 35.55 | 0.86
12 | 3.5 | 0 | 6.31 | 15.39 | 0 |  |  | 0.3 | 0.02 | 1.97 | 17.8 | 11.77
13 | 2.91 | 0 | 1.35 | 2.27 | 0 |  |  | 0.01 | 0.04 | 0.25 | 14.49 | 9.43
14 | 0.58 | 0 | 4.54 | 5.98 | 0 |  |  | 0.06 | 0.02 | 0.09 | 0.49 | 6.85
15 | 2.56 | 0 | 0.53 | 10.71 | 1.28 |  |  | 4.02 | 3.82 | 2.04 | 2.36 | 1.64
16 | 0.65 | 0 | 0 | 1.09 | 8.14 |  |  | 4.73 | 0.3 | 0.05 | 42.01 | 0.19
17 | 0 | 0 | 0.43 | 1.44 | 1.14 |  |  | 1.66 | 6.19 | 1.09 | 15.81 | 6.22
18 | 14.67 | 0 | 0.19 | 5.38 | 1.68 |  |  | 0.34 | 13.03 | 0.58 | 0.01 | 8.79
19 | 13.76 | 0 | 2.14 | 4.23 | 4.27 |  |  | 8.34 | 15.43 | 6.43 | 2.1 | 3.48
20 | 16.42 | 0 | 4.65 | 0.81 | 22.01 |  |  | 0.33 | 2.47 | 0.01 | 0.25 | 0.52
21 | 2.55 | 0 | 1.52 | 4.25 | 0.33 |  |  | 0.07 | 1.13 | 1.22 | 0.4 | 7.93
22 | 0.42 | 0 | 0.41 | 18.14 | 10.26 |  |  | 0 | 0.38 | 14.08 | 7.05 | 0.55
23 | 1.32 | 0 | 0 | 0.62 | 0.52 |  |  | 3.89 | 0 | 10.62 | 3.89 | 0.61
24 | 0 | 0 | 0 | 6.58 | 16.25 |  |  | 1.19 | 0 | 2.74 | 5.19 | 2.16
25 | 0.79 | 0 | 0.02 | 4.64 | 0.34 |  |  | 0.5 | 0 | 0.13 | 4.8 | 6.34
26 | 4.22 | 0 | 0 | 2.44 | 1.69 |  |  | 0.98 | 5.93 | 0 | 6.01 | 3.3
27 | 4.41 | 0 | 7.39 | 1.19 | 0.78 |  |  | 0.01 | 11.23 | 15.01 | 38.51 | 3.27
28 | 4.06 | 0 | 8.02 | 0.66 | 3.29 |  |  | 1.12 | 1.22 | 7.6 | 1.93 | 2.01
29 | 0.49 | 0 | 1.21 | 0.71 | 2.72 |  |  | 4.24 | 2.78 |  | 1.86 | 0.04
30 | 0 | 0 | 1.07 | 16.54 | 0.72 |  |  | 37.6 |  |  | 0.05 | 4.08
31 | July: 0; Aug.: 0; Oct.: 3.05; Jan.: 5.45; May: 1.1
Total | 121.16 | 8.63 | 43.49 | 129.11 | 134.98 |  |  | 110.51 | 108.75 | 91.78 | 234.79 | 155.01

## Fuel Cost Comparisons
Heating Fuel Cost Comparisons - 2007/08
| Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | AVG.
Quoted Price
Natural Gas - $/MCF |  | 6.3398 | 7.47 | 8.0354 | 7.82 | 8.27 | 9.245 | 9.52 | 11.16 | 8.4825
#2 Fuel Oil - $/Gal |  |  |  |  | 2.83 | 2.91 | 3.04 | 3.34 | 3.446 | 1.9458
#6 Fuel Oil - $/Gal |  | 1 | 1.05 | 1.2 | 0.92 | 1.12 | 1.29 | 1.34 | 1.54 | 1.1825
Fuel Used |  | Nat Gas | Nat Gas | Nat Gas | F.O./Nat Gas | Nat Gas | Nat Gas | Nat Gas | Nat Gas
Comparitive Price per Million BTUs
Natural Gas |  | 7.73 | 9.1 | 9.79 | 9.53 | 10.09 | 11.27 | 11.6 | 13.61 | 10.34
#2 Fuel Oil |  |  |  |  | 23.67 | 24.34 | 25.43 | 27.96 | 28.83 | 16.2787
#6 Fuel Oil |  | 8.89 | 9.33 | 10.66 | 8.17 | 9.95 | 11.46 | 11.9 | 13.68 | 10.505
NOTE: The costs expressed are for 1,000,000 btus. The unit price of each fuel is converted to reflect the cost
to burn 1 million btus of each fuel type.
Premium to Burn Gas vs. #6 Fuel Oil
Total BTU's
QTY-BTU (x 1000) | AVG.: 0
Nat. Gas @ $0.00/mil BTU's= | Sept: 0
#6 Fuel Oil @ $0.00/mil BTU's= | Sept: 0
Premium to burn gas= | Sept: 0